## CALCULATOR
Calculate Efficiency and Fuel Savings of Your System! Balance Capital Costs with Payback from Energy Savings!
Instruction: Enter system information in the yellow fields. View results in green fields.
STEP 1 |  | STEP 5
LOCATION |  | FUEL COSTS
CITY | SYRACUSE | EFFICIENCY OF OLD BOILERS TO BE REPLACED | 82%
STATE | NY | NATURAL GAS RATE [$/Therm] | 2
HEATING DESIGN TEMPERATURE | -3 | ANNUAL FUEL COST ESCALATOR | 3%
|  | THERMS BURNED PER YEAR, NEW FULTON BOILERS | 343932.7228
STEP 2 |  | THERMS BURNED PER YEAR, OLD BOILERS | 400143.6686
LOAD REQUIREMENTS |  | ANNUAL FUEL COST, NEW FULTON BOILERS | 687865.4455
BUILDING LOAD AT DESIGN TEMPERATURE | 12000000 | ANNUAL FUEL COST, OLD BOILER(S) | 800287.3371
|  | ANNUAL COST SAVING OVER OLD BOILER SYSTEM | 112421.8916
STEP 3 |  | 20 YEAR FUEL COST, NEW FULTON BOILERS | 17277025.8966
BOILERS |  | 20 YEAR FUEL COST, OLD BOILER(S) | 21504020.4472
FULTON HEATING SOLUTIONS BOILER MODEL | VTG-4000 | 20 YEAR COST SAVING OVER OLD BOILER SYSTEM | 4226994.5506
NUMBER OF FULTON BOILERS CHOSEN | 4
DELTA-T ACROSS BOILER INLET/OUTLET | 20 | STEP 6
TOTAL MAX INPUT CAPACITY | 16000000 | BOILER RETURN ON INVESTMENT
|  | INDIVIDUAL BOILER COST | 60000
STEP 4 |  | CONTROLS COSTS | 8000
OUTDOOR RESET SCHEDULE |  | INSTALLATION COST | 80000
WARM WEATHER SHUTDOWN TEMPERATURE | 64 | TOTAL CAPITAL INVESTMENT | 328000
OUTDOOR T1 | 0 | PAY-BACK PERIOD OF COMPLETE CAPITAL INVESTMENT [years] | 2.9176
WATER T1 | 170
OUTDOOR T2 | 55 | NOTE: This calculator is designed for use by Fulton representatives for simple analysis. This is not an engineering design tool. Fulton cannot be held responsible for actual system performance.
WATER T2 | 90
AVERAGE ANNUAL EFFICIENCY OF FULTON BOILERS | 97.43%

## CLIMATIC DATA (hidden)
MEAN TEMPERATURE | [13 empty] | DESIGN T | TEMPERATURE RANGE | [11 empty] | MAX TEMPERATURE | [11 empty] | MIN TEMPERATURE
|  | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC |  | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC
ALBANY | NY | 20.6 | 23.5 | 34.3 | 46.4 | 57.6 | 66.9 | 71.8 | 69.6 | 61.3 | 50.2 | 39.7 | 26.5 | -2.9 | 15.3 | 16.8 | 17.7 | 19.7 | 20.6 | 20.2 | 20 | 19.4 | 19.7 | 19.1 | 15.6 | 14 | 28.25 | 31.9 | 43.15 | 56.25 | 67.9 | 77 | 81.8 | 79.3 | 71.15 | 59.75 | 47.5 | 33.5 | 12.95 | 15.1 | 25.45 | 36.55 | 47.3 | 56.8 | 61.8 | 59.9 | 51.45 | 40.65 | 31.9 | 19.5
ALBUQUERQUE | NM | 34.2 | 40 | 46.9 | 55.2 | 64.2 | 74.2 | 78.5 | 75.9 | 68.6 | 57 | 44.3 | 35.3 | 15.9 | 21.1 | 22.7 | 25.1 | 26.3 | 26.7 | 27 | 24.4 | 22.7 | 23.4 | 23.6 | 21.9 | 20.2 | 44.75 | 51.35 | 59.45 | 68.35 | 77.55 | 87.7 | 90.7 | 87.25 | 80.3 | 68.8 | 55.25 | 45.4 | 23.65 | 28.65 | 34.35 | 42.05 | 50.85 | 60.7 | 66.3 | 64.55 | 56.9 | 45.2 | 33.35 | 25.2
ANCHORAGE | AK | 14.9 | 18.7 | 25.7 | 35.8 | 46.6 | 54.4 | 58.4 | 56.3 | 48.4 | 34.6 | 21.2 | 16.3 | -10.7 | 10.3 | 11.3 | 13.1 | 13.9 | 14.5 | 13.7 | 11.9 | 12.1 | 11.6 | 10.1 | 9.6 | 10 | 20.05 | 24.35 | 32.25 | 42.75 | 53.85 | 61.25 | 64.35 | 62.35 | 54.2 | 39.65 | 26 | 21.3 | 9.75 | 13.05 | 19.15 | 28.85 | 39.35 | 47.55 | 52.45 | 50.25 | 42.6 | 29.55 | 16.4 | 11.3
ASHEVILLE | NC | 35.7 | 38.7 | 47.4 | 55.2 | 63 | 69.4 | 72.8 | 72 | 66.2 | 55.9 | 47.5 | 39.5 | 12.2 | 19.6 | 20 | 21.8 | 23.2 | 22.2 | 20.1 | 19.2 | 18.6 | 19.7 | 22.3 | 21.5 | 19.7 | 45.5 | 48.7 | 58.3 | 66.8 | 74.1 | 79.45 | 82.4 | 81.3 | 76.05 | 67.05 | 58.25 | 49.35 | 25.9 | 28.7 | 36.5 | 43.6 | 51.9 | 59.35 | 63.2 | 62.7 | 56.35 | 44.75 | 36.75 | 29.65
ATLANTA | GA | 41 | 44.8 | 53.5 | 61.5 | 69.2 | 76 | 78.8 | 78.1 | 72.7 | 62.3 | 53.1 | 44.5 | 18.8 | 17.4 | 17.8 | 19.5 | 20.1 | 18.8 | 17.3 | 17.1 | 16.4 | 16.5 | 17.8 | 18.1 | 17 | 49.7 | 53.7 | 63.25 | 71.55 | 78.6 | 84.65 | 87.35 | 86.3 | 80.95 | 71.2 | 62.15 | 53 | 32.3 | 35.9 | 43.75 | 51.45 | 59.8 | 67.35 | 70.25 | 69.9 | 64.45 | 53.4 | 44.05 | 36
AUGUSTA | ME | 43.9 | 47.4 | 55.5 | 62.7 | 70.7 | 77.5 | 80.8 | 79.7 | 74.5 | 63.8 | 55 | 47.2 | -3.4 | 15.3 | 16.2 | 15.8 | 17.3 | 19 | 18.7 | 18.2 | 18.3 | 17.9 | 16.5 | 13.4 | 13.9 | 51.55 | 55.5 | 63.4 | 71.35 | 80.2 | 86.85 | 89.9 | 88.85 | 83.45 | 72.05 | 61.7 | 54.15 | 36.25 | 39.3 | 47.6 | 54.05 | 61.2 | 68.15 | 71.7 | 70.55 | 65.55 | 55.55 | 48.3 | 40.25
AUSTIN | TX | 48.8 | 52.8 | 61.5 | 69.6 | 75.6 | 81.3 | 84.5 | 84.8 | 80.2 | 71.1 | 60.9 | 51.6 | 25.7 | 21.2 | 21.2 | 21.6 | 21.2 | 19.7 | 19.9 | 21.1 | 22.5 | 21.7 | 21.9 | 21.6 | 21.9 | 59.4 | 63.4 | 72.3 | 80.2 | 85.45 | 91.25 | 95.05 | 96.05 | 91.05 | 82.05 | 71.7 | 62.55 | 38.2 | 42.2 | 50.7 | 59 | 65.75 | 71.35 | 73.95 | 73.55 | 69.35 | 60.15 | 50.1 | 40.65
BALTIMORE | MD | 31.8 | 34.8 | 44.1 | 53.4 | 63.4 | 72.5 | 77 | 75.6 | 68.5 | 56.6 | 46.8 | 36.7 | 12.3 | 15.5 | 16.7 | 18.4 | 20.3 | 20.2 | 19.6 | 18.7 | 18.3 | 18.6 | 19.8 | 18.6 | 16 | 39.55 | 43.15 | 53.3 | 63.55 | 73.5 | 82.3 | 86.35 | 84.75 | 77.8 | 66.5 | 56.1 | 44.7 | 24.05 | 26.45 | 34.9 | 43.25 | 53.3 | 62.7 | 67.65 | 66.45 | 59.2 | 46.7 | 37.5 | 28.7
BILLINGS | MT | 22.8 | 29 | 35.5 | 45.6 | 55 | 64.8 | 72.5 | 70.7 | 59.1 | 49.1 | 35.1 | 25.5 | -12.7 | 16.9 | 18.3 | 19.9 | 21.4 | 22.4 | 23.4 | 26.1 | 26.6 | 23.6 | 21.1 | 17.2 | 16.1 | 31.25 | 38.15 | 45.45 | 56.3 | 66.2 | 76.5 | 85.55 | 84 | 70.9 | 59.65 | 43.7 | 33.55 | 14.35 | 19.85 | 25.55 | 34.9 | 43.8 | 53.1 | 59.45 | 57.4 | 47.3 | 38.55 | 26.5 | 17.45
BIRMINGHAM | AL | 41.5 | 45.7 | 54.2 | 62 | 69.4 | 76.3 | 79.8 | 79 | 73.4 | 62.5 | 53.1 | 45.2 | 18.6 | 19.3 | 20.2 | 22.1 | 23 | 21.1 | 19.3 | 18.6 | 19.2 | 20.2 | 21.7 | 20.7 | 19.1 | 51.15 | 55.8 | 65.25 | 73.5 | 79.95 | 85.95 | 89.1 | 88.6 | 83.5 | 73.35 | 63.45 | 54.75 | 31.85 | 35.6 | 43.15 | 50.5 | 58.85 | 66.65 | 70.5 | 69.4 | 63.3 | 51.65 | 42.75 | 35.65
BISMARK | ND | 9.2 | 15.7 | 28.2 | 43 | 55 | 64.4 | 70.4 | 68.3 | 57 | 45.7 | 28.6 | 14 | -20.8 | 19.2 | 19.1 | 19.4 | 24.4 | 24.1 | 23.5 | 25.6 | 26.5 | 25.4 | 24.2 | 19 | 18.8 | 18.8 | 25.25 | 37.9 | 55.2 | 67.05 | 76.15 | 83.2 | 81.55 | 69.7 | 57.8 | 38.1 | 23.4 | -0.4 | 6.15 | 18.5 | 30.8 | 42.95 | 52.65 | 57.6 | 55.05 | 44.3 | 33.6 | 19.1 | 4.6
BOISE | ID | 29 | 35.9 | 42.4 | 49.1 | 57.5 | 66.5 | 74 | 72.5 | 62.6 | 51.8 | 39.9 | 30.1 | 1.6 | 13 | 16.2 | 19.8 | 22.4 | 24.5 | 27 | 30 | 29.5 | 27 | 23.8 | 15.8 | 13.2 | 35.5 | 44 | 52.3 | 60.3 | 69.75 | 80 | 89 | 87.25 | 76.1 | 63.7 | 47.8 | 36.7 | 22.5 | 27.8 | 32.5 | 37.9 | 45.25 | 53 | 59 | 57.75 | 49.1 | 39.9 | 32 | 23.5
BOSTON | MA | 28.6 | 30.3 | 38.6 | 48.1 | 58.2 | 67.7 | 73.5 | 71.9 | 64.8 | 54.8 | 45.3 | 33.6 | 7.7 | 13.1 | 13.4 | 13.7 | 14.2 | 15 | 15.7 | 15.2 | 14.2 | 14.3 | 14.3 | 13.2 | 12.6 | 35.15 | 37 | 45.45 | 55.2 | 65.7 | 75.55 | 81.1 | 79 | 71.95 | 61.95 | 51.9 | 39.9 | 22.05 | 23.6 | 31.75 | 41 | 50.7 | 59.85 | 65.9 | 64.8 | 57.65 | 47.65 | 38.7 | 27.3
BUFFALO | NY | 23.6 | 24.5 | 33.8 | 45.2 | 56.6 | 65.9 | 71.1 | 69 | 61.9 | 51.1 | 40.5 | 29.1 | 2.2 | 12.4 | 13.6 | 15.3 | 17.2 | 18 | 17.3 | 16.8 | 16.8 | 16.9 | 15.5 | 12.8 | 11.6 | 29.8 | 31.3 | 41.45 | 53.8 | 65.6 | 74.55 | 79.5 | 77.4 | 70.35 | 58.85 | 46.9 | 34.9 | 17.4 | 17.7 | 26.15 | 36.6 | 47.6 | 57.25 | 62.7 | 60.6 | 53.45 | 43.35 | 34.1 | 23.3
BURLINGTON | VT | 16.3 | 18.2 | 30.7 | 43.9 | 56.3 | 65.2 | 70.5 | 67.9 | 58.9 | 47.8 | 36.8 | 23 | -9.3 | 15.8 | 17.2 | 16.9 | 18.4 | 20 | 19.7 | 19.3 | 19.1 | 18.4 | 16.7 | 13.5 | 13.8 | 24.2 | 26.8 | 39.15 | 53.1 | 66.3 | 75.05 | 80.15 | 77.45 | 68.1 | 56.15 | 43.55 | 29.9 | 8.4 | 9.6 | 22.25 | 34.7 | 46.3 | 55.35 | 60.85 | 58.35 | 49.7 | 39.45 | 30.05 | 16.1
CALGARY | ALBERTA | 15.98 | 21.02 | 28.58 | 40.28 | 49.64 | 56.84 | 61.16 | 60.08 | 51.44 | 41.72 | 26.42 | 18.68 | -20.6 | 19.5 | 19.8 | 19.2 | 21.8 | 21.8 | 20.3 | 22.2 | 23.3 | 22.5 | 21.7 | 18.5 | 19.1 | 25.73 | 30.92 | 38.18 | 51.18 | 60.54 | 66.99 | 72.26 | 71.73 | 62.69 | 52.57 | 35.67 | 28.23 | 6.23 | 11.12 | 18.98 | 29.38 | 38.74 | 46.69 | 50.06 | 48.43 | 40.19 | 30.87 | 17.17 | 9.13
CAHARLESTON - SC | SC | 47.8 | 50.5 | 58.1 | 64.9 | 72.8 | 78.3 | 81.5 | 80.6 | 76.4 | 66.8 | 58.4 | 51.2 | 25.4 | 19.3 | 19.8 | 20.4 | 20.8 | 19.2 | 16.6 | 16.2 | 15.6 | 15.6 | 18.3 | 20.1 | 19.5 | 57.45 | 60.4 | 68.3 | 75.3 | 82.4 | 86.6 | 89.6 | 88.4 | 84.2 | 75.95 | 68.45 | 60.95 | 38.15 | 40.6 | 47.9 | 54.5 | 63.2 | 70 | 73.4 | 72.8 | 68.6 | 57.65 | 48.35 | 41.45
CHARLESTON - WV | WV | 47.8 | 50.5 | 58.1 | 64.9 | 72.8 | 78.3 | 81.5 | 80.6 | 76.4 | 66.8 | 58.4 | 51.2 | 6.7 | 16.6 | 18 | 20.7 | 22.8 | 21.9 | 20.5 | 19.2 | 19.7 | 20.5 | 21.7 | 19.5 | 16.6 | 56.1 | 59.5 | 68.45 | 76.3 | 83.75 | 88.55 | 91.1 | 90.45 | 86.65 | 77.65 | 68.15 | 59.5 | 39.5 | 41.5 | 47.75 | 53.5 | 61.85 | 68.05 | 71.9 | 70.75 | 66.15 | 55.95 | 48.65 | 42.9
CHARLOTTE | NC | 39.3 | 42.5 | 50.9 | 59.4 | 67.4 | 75.7 | 79.3 | 78.3 | 72.4 | 61.3 | 52.1 | 42.6 | 19 | 18.2 | 19.3 | 20.8 | 21.8 | 20.4 | 18.7 | 18.2 | 17.6 | 18 | 20 | 20.1 | 18.4 | 48.4 | 52.15 | 61.3 | 70.3 | 77.6 | 85.05 | 88.4 | 87.1 | 81.4 | 71.3 | 62.15 | 51.8 | 30.2 | 32.85 | 40.5 | 48.5 | 57.2 | 66.35 | 70.2 | 69.5 | 63.4 | 51.3 | 42.05 | 33.4
CHARLOTTETOWN | P. EDWARD ISLAND | 17.6 | 17.96 | 26.42 | 36.86 | 48.38 | 58.28 | 65.3 | 64.58 | 56.48 | 46.04 | 36.14 | 24.62 | -5.2 | 14.6 | 14.8 | 13.1 | 13.4 | 16.9 | 16.2 | 14.9 | 14.5 | 14.3 | 12.7 | 11 | 12.3 | 24.9 | 25.36 | 32.97 | 43.56 | 56.83 | 66.38 | 72.75 | 71.83 | 63.63 | 52.39 | 41.64 | 30.77 | 10.3 | 10.56 | 19.87 | 30.16 | 39.93 | 50.18 | 57.85 | 57.33 | 49.33 | 39.69 | 30.64 | 18.47
CHEYENNE | WY | 26.5 | 29.3 | 33.6 | 42.5 | 52 | 61.3 | 68.4 | 66.4 | 57.4 | 47 | 35.2 | 27.8 | -6.2 | 20 | 20.5 | 21.5 | 22.7 | 23.4 | 24.9 | 26.3 | 25.5 | 25.4 | 23.7 | 20.5 | 19.5 | 36.5 | 39.55 | 44.35 | 53.85 | 63.7 | 73.75 | 81.55 | 79.15 | 70.1 | 58.85 | 45.45 | 37.55 | 16.5 | 19.05 | 22.85 | 31.15 | 40.3 | 48.85 | 55.25 | 53.65 | 44.7 | 35.15 | 24.95 | 18.05
CHICAGO | IL | 21 | 25.4 | 37.2 | 48.6 | 58.9 | 68.6 | 73.2 | 71.7 | 64.4 | 52.8 | 40 | 26.6 | -5 | 12.4 | 12.9 | 14.8 | 17 | 18 | 17.5 | 15.9 | 14.9 | 16.5 | 16.1 | 13.3 | 12 | 27.2 | 31.85 | 44.6 | 57.1 | 67.9 | 77.35 | 81.15 | 79.15 | 72.65 | 60.85 | 46.65 | 32.6 | 14.8 | 18.95 | 29.8 | 40.1 | 49.9 | 59.85 | 65.25 | 64.25 | 56.15 | 44.75 | 33.35 | 20.6
COLUMBIA | SC | 43.8 | 46.8 | 55.2 | 63 | 70.9 | 77.4 | 80.8 | 79.7 | 74.2 | 63.3 | 54.6 | 46.9 | 20.8 | 21.2 | 22.2 | 24 | 24.5 | 23.3 | 20.7 | 20 | 18.9 | 19.7 | 22.9 | 23.7 | 22 | 54.4 | 57.9 | 67.2 | 75.25 | 82.55 | 87.75 | 90.8 | 89.15 | 84.05 | 74.75 | 66.45 | 57.9 | 33.2 | 35.7 | 43.2 | 50.75 | 59.25 | 67.05 | 70.8 | 70.25 | 64.35 | 51.85 | 42.75 | 35.9
COLUMBUS | OH | 26.4 | 29.6 | 40.9 | 51 | 61.2 | 69.2 | 73.2 | 71.5 | 65.5 | 53.7 | 42.9 | 31.9 | 1.4 | 13.9 | 15.5 | 18 | 20.4 | 20.1 | 19.4 | 18.8 | 19 | 20 | 19.6 | 15.8 | 13.2 | 33.35 | 37.35 | 49.9 | 61.2 | 71.25 | 78.9 | 82.6 | 81 | 75.5 | 63.5 | 50.8 | 38.5 | 19.45 | 21.85 | 31.9 | 40.8 | 51.15 | 59.5 | 63.8 | 62 | 55.5 | 43.9 | 35 | 25.3
CONCORD | NH | 18.6 | 21.8 | 32.4 | 43.9 | 55.2 | 64.2 | 69.5 | 67.3 | 58.8 | 47.8 | 37.1 | 24.3 | -6.2 | 18.6 | 19.9 | 19.8 | 22.7 | 24.2 | 23.4 | 23.1 | 23 | 23.6 | 23.2 | 18.8 | 17.9 | 27.9 | 31.75 | 42.3 | 55.25 | 67.3 | 75.9 | 81.05 | 78.8 | 70.6 | 59.4 | 46.5 | 33.25 | 9.3 | 11.85 | 22.5 | 32.55 | 43.1 | 52.5 | 57.95 | 55.8 | 47 | 36.2 | 27.7 | 15.35
DALLAS | TX | 43.4 | 47.9 | 56.7 | 65.5 | 72.8 | 81 | 85.3 | 84.9 | 77.4 | 67.2 | 56.2 | 46.9 | 19.9 | 19.6 | 19.5 | 20 | 20.3 | 18.4 | 18.8 | 19.7 | 19.8 | 20 | 20.3 | 19.2 | 18.6 | 53.2 | 57.65 | 66.7 | 75.65 | 82 | 90.4 | 95.15 | 94.8 | 87.4 | 77.35 | 65.8 | 56.2 | 33.6 | 38.15 | 46.7 | 55.35 | 63.6 | 71.6 | 75.45 | 75 | 67.4 | 57.05 | 46.6 | 37.6
DAYTON | OH | 26 | 29.4 | 40.5 | 51.2 | 61.7 | 70.4 | 74.2 | 72.2 | 65.8 | 54.1 | 42.9 | 31.6 | -0.6 | 14 | 15.3 | 17.5 | 19.6 | 19 | 18.5 | 18.5 | 18.8 | 20 | 18.8 | 15.5 | 13.3 | 33 | 37.05 | 49.25 | 61 | 71.2 | 79.65 | 83.45 | 81.6 | 75.8 | 63.5 | 50.65 | 38.25 | 19 | 21.75 | 31.75 | 41.4 | 52.2 | 61.15 | 64.95 | 62.8 | 55.8 | 44.7 | 35.15 | 24.95
DAYTONA BEACH | FL | 57.5 | 59 | 64.3 | 69.3 | 74.7 | 79.4 | 81.2 | 81 | 79.4 | 73.4 | 65.9 | 60.1 | 34 | 19.9 | 19.2 | 19.1 | 19.3 | 18.3 | 15.8 | 16.2 | 15.4 | 13.6 | 14.9 | 17.3 | 18.6 | 67.45 | 68.6 | 73.85 | 78.95 | 83.85 | 87.3 | 89.3 | 88.7 | 86.2 | 80.85 | 74.55 | 69.4 | 47.55 | 49.4 | 54.75 | 59.65 | 65.55 | 71.5 | 73.1 | 73.3 | 72.6 | 65.95 | 57.25 | 50.8
DENVER | CO | 29.7 | 33.4 | 39 | 48.2 | 57.2 | 66.9 | 73.5 | 71.4 | 62.3 | 51.4 | 39 | 31 | -4 | 23.7 | 23.9 | 25.8 | 25.1 | 25.8 | 27.4 | 27.4 | 26.6 | 26.9 | 25.8 | 24.1 | 22.7 | 41.55 | 45.35 | 51.9 | 60.75 | 70.1 | 80.6 | 87.2 | 84.7 | 75.75 | 64.3 | 51.05 | 42.35 | 17.85 | 21.45 | 26.1 | 35.65 | 44.3 | 53.2 | 59.8 | 58.1 | 48.85 | 38.5 | 26.95 | 19.65
DES MOINES | IA | 19.4 | 24.7 | 37.3 | 50.9 | 62.3 | 71.8 | 76.6 | 73.9 | 65.1 | 53.5 | 39 | 24.4 | -7.8 | 15.9 | 16.5 | 18.5 | 20.1 | 19.1 | 18.7 | 18.2 | 18.2 | 20.1 | 19.4 | 16.6 | 15.4 | 27.35 | 32.95 | 46.55 | 60.95 | 71.85 | 81.15 | 85.7 | 83 | 75.15 | 63.2 | 47.3 | 32.1 | 11.45 | 16.45 | 28.05 | 40.85 | 52.75 | 62.45 | 67.5 | 64.8 | 55.05 | 43.8 | 30.7 | 16.7
DETROIT | MI | 22.9 | 25.4 | 35.7 | 47.3 | 58.4 | 67.6 | 72.3 | 70.5 | 63.2 | 51.2 | 40.2 | 28.3 | 3.4 | 11.5 | 12.8 | 15.4 | 17.8 | 18.7 | 18.2 | 17.5 | 16.5 | 17.1 | 15.5 | 12.3 | 10.5 | 28.65 | 31.8 | 43.4 | 56.2 | 67.75 | 76.7 | 81.05 | 78.75 | 71.75 | 58.95 | 46.35 | 33.55 | 17.15 | 19 | 28 | 38.4 | 49.05 | 58.5 | 63.55 | 62.25 | 54.65 | 43.45 | 34.05 | 23.05
DOVER | DE | 30.6 | 33.4 | 42.7 | 52.2 | 62.5 | 71.5 | 76.4 | 75 | 68 | 56.2 | 46.3 | 35.8 | 13.8 | 14.5 | 15.3 | 16.8 | 17.9 | 17.6 | 17.1 | 16.4 | 15.8 | 16.3 | 17.3 | 16.6 | 14.9 | 37.85 | 41.05 | 51.1 | 61.15 | 71.3 | 80.05 | 84.6 | 82.9 | 76.15 | 64.85 | 54.6 | 43.25 | 23.35 | 25.75 | 34.3 | 43.25 | 53.7 | 62.95 | 68.2 | 67.1 | 59.85 | 47.55 | 38 | 28.35
DULUTH | MN | 7 | 12.3 | 24.4 | 38.6 | 50.8 | 59.8 | 66.1 | 63.7 | 54.2 | 43.7 | 28.4 | 12.8 | -20.2 | 16.2 | 16.7 | 15.5 | 18 | 20.1 | 20.1 | 19.6 | 18.4 | 17.5 | 15.7 | 12.7 | 14 | 15.1 | 20.65 | 32.15 | 47.6 | 60.85 | 69.85 | 75.9 | 72.9 | 62.95 | 51.55 | 34.75 | 19.8 | -1.1 | 3.95 | 16.65 | 29.6 | 40.75 | 49.75 | 56.3 | 54.5 | 45.45 | 35.85 | 22.05 | 5.8
EVANSVILLE | IN | 30.1 | 34.4 | 45.8 | 56.2 | 65.5 | 74.8 | 78.4 | 76.1 | 69.2 | 57.2 | 46.2 | 35.2 | 3.7 | 15.2 | 17 | 19.3 | 20.9 | 20.4 | 19.7 | 19.1 | 20.3 | 22.2 | 22.3 | 18.1 | 15.4 | 37.7 | 42.9 | 55.45 | 66.65 | 75.7 | 84.65 | 87.95 | 86.25 | 80.3 | 68.35 | 55.25 | 42.9 | 22.5 | 25.9 | 36.15 | 45.75 | 55.3 | 64.95 | 68.85 | 65.95 | 58.1 | 46.05 | 37.15 | 27.5
FAIRBANKS | AK | -10.1 | -3.6 | 11 | 30.7 | 48.6 | 59.8 | 62.5 | 56.8 | 45.5 | 25.1 | 2.7 | -6.5 | -48 | 15 | 19.1 | 24.9 | 21.2 | 20.6 | 20.1 | 18.4 | 17.2 | 17.3 | 13.3 | 14 | 15.2 | -2.6 | 5.95 | 23.45 | 41.3 | 58.9 | 69.85 | 71.7 | 65.4 | 54.15 | 31.75 | 9.7 | 1.1 | -17.6 | -13.15 | -1.45 | 20.1 | 38.3 | 49.75 | 53.3 | 48.2 | 36.85 | 18.45 | -4.3 | -14.1
FARGO | ND | 5.9 | 12 | 25.9 | 43 | 56.2 | 65.5 | 71.1 | 68.8 | 57.7 | 45.7 | 28.1 | 11.6 | -21.1 | 16.8 | 16.6 | 15.4 | 21.5 | 22.5 | 21 | 21.3 | 22.3 | 21.7 | 19.8 | 15.5 | 15.1 | 14.3 | 20.3 | 33.6 | 53.75 | 67.45 | 76 | 81.75 | 79.95 | 68.55 | 55.6 | 35.85 | 19.15 | -2.5 | 3.7 | 18.2 | 32.25 | 44.95 | 55 | 60.45 | 57.65 | 46.85 | 35.8 | 20.35 | 4.05
FLINT | MI | 21.5 | 23.5 | 34 | 46 | 56.8 | 65.9 | 70.6 | 68.6 | 61.4 | 50.1 | 39.4 | 27.2 | -1.7 | 13.2 | 14.8 | 17.2 | 20 | 21.3 | 21.3 | 21 | 20.1 | 20.9 | 18.7 | 14.1 | 12.1 | 28.1 | 30.9 | 42.6 | 56 | 67.45 | 76.55 | 81.1 | 78.65 | 71.85 | 59.45 | 46.45 | 33.25 | 14.9 | 16.1 | 25.4 | 36 | 46.15 | 55.25 | 60.1 | 58.55 | 50.95 | 40.75 | 32.35 | 21.15
FORTH WAINE | IN | 22.9 | 25.9 | 37.6 | 49.2 | 60.2 | 70.2 | 74 | 71.6 | 64.9 | 52.9 | 41.3 | 28.6 | -3.6 | 13.6 | 14.6 | 17.6 | 20.5 | 20.7 | 20.2 | 20 | 19.6 | 21.7 | 19.8 | 15.2 | 12.8 | 29.7 | 33.2 | 46.4 | 59.45 | 70.55 | 80.3 | 84 | 81.4 | 75.75 | 62.8 | 48.9 | 35 | 16.1 | 18.6 | 28.8 | 38.95 | 49.85 | 60.1 | 64 | 61.8 | 54.05 | 43 | 33.7 | 22.2
FRESNO | CA | 45.7 | 51.2 | 55.1 | 61.2 | 69 | 76.6 | 81.9 | 80.3 | 74.5 | 65.2 | 53.6 | 45.4 | 30.7 | 14.8 | 18.8 | 20.5 | 24.1 | 26.8 | 28.7 | 29.5 | 29.7 | 28.1 | 25.5 | 20 | 15.7 | 53.1 | 60.6 | 65.35 | 73.25 | 82.4 | 90.95 | 96.65 | 95.15 | 88.55 | 77.95 | 63.6 | 53.25 | 38.3 | 41.8 | 44.85 | 49.15 | 55.6 | 62.25 | 67.15 | 65.45 | 60.45 | 52.45 | 43.6 | 37.55
GRAND RAPIDS | MI | 21.8 | 23.7 | 34.1 | 46 | 57.5 | 67 | 71.6 | 69.5 | 61 | 49.5 | 38 | 27.1 | 0.3 | 12.1 | 13.3 | 16.5 | 19.6 | 20.7 | 20.6 | 19.9 | 18.7 | 19.6 | 17.8 | 13.3 | 11.1 | 27.85 | 30.35 | 42.35 | 55.8 | 67.85 | 77.3 | 81.55 | 78.85 | 70.8 | 58.4 | 44.65 | 32.65 | 15.75 | 17.05 | 25.85 | 36.2 | 47.15 | 56.7 | 61.65 | 60.15 | 51.2 | 40.6 | 31.35 | 21.55
GREENSBORO | NC | 36.7 | 40 | 48.8 | 57.6 | 65.9 | 73.1 | 76.9 | 75.7 | 69.7 | 58.6 | 49.5 | 40.5 | 15 | 17.7 | 19 | 20.7 | 21.8 | 20.4 | 18.5 | 17.8 | 17.3 | 18 | 20.3 | 20 | 18 | 45.55 | 49.5 | 59.15 | 68.5 | 76.1 | 82.35 | 85.8 | 84.35 | 78.7 | 68.75 | 59.5 | 49.5 | 27.85 | 30.5 | 38.45 | 46.7 | 55.7 | 63.85 | 68 | 67.05 | 60.7 | 48.45 | 39.5 | 31.5
GREENVILLE | SC | 40.1 | 43.4 | 51.7 | 59.8 | 67.9 | 75 | 78.2 | 77.1 | 71.2 | 60.5 | 51.6 | 43.3 | 19.5 | 18.4 | 19.3 | 21.3 | 22.4 | 21.2 | 19.5 | 19 | 18 | 18.5 | 20.4 | 20 | 18.4 | 49.3 | 53.05 | 62.35 | 71 | 78.5 | 84.75 | 87.7 | 86.1 | 80.45 | 70.7 | 61.6 | 52.5 | 30.9 | 33.75 | 41.05 | 48.6 | 57.3 | 65.25 | 68.7 | 68.1 | 61.95 | 50.3 | 41.6 | 34.1
HALIFAX | NOVA SCOTIA | 21.2 | 21.92 | 29.48 | 39.2 | 49.64 | 59 | 65.48 | 65.12 | 57.38 | 46.94 | 37.58 | 26.96 | -1.4 | 15.1 | 15.3 | 14.4 | 15 | 17.4 | 17.5 | 16.7 | 15.9 | 15.7 | 14.4 | 12.4 | 13.5 | 28.75 | 29.57 | 36.68 | 46.7 | 58.34 | 67.75 | 73.83 | 73.07 | 65.23 | 54.14 | 43.78 | 33.71 | 13.65 | 14.27 | 22.28 | 31.7 | 40.94 | 50.25 | 57.13 | 57.17 | 49.53 | 39.74 | 31.38 | 20.21
HARRISBURG | PA | 28.6 | 31.3 | 41.2 | 51.6 | 61.8 | 70.9 | 75.7 | 74.1 | 66.4 | 54.7 | 44.4 | 33.6 | 8.3 | 14 | 15.2 | 17.9 | 19.6 | 20.3 | 19.8 | 19.4 | 18.6 | 19.2 | 18.8 | 17.1 | 14.2 | 35.6 | 38.9 | 50.15 | 61.4 | 71.95 | 80.8 | 85.4 | 83.4 | 76 | 64.1 | 52.95 | 40.7 | 21.6 | 23.7 | 32.25 | 41.8 | 51.65 | 61 | 66 | 64.8 | 56.8 | 45.3 | 35.85 | 26.5
HARTFORD | CT | 24.6 | 27.5 | 37.5 | 48.7 | 59.6 | 68.5 | 73.7 | 71.6 | 63.3 | 52.2 | 41.9 | 29.5 | 2.9 | 15.3 | 16.5 | 18.3 | 20.4 | 21.6 | 21.2 | 20.5 | 20.1 | 20.7 | 20.6 | 17.2 | 15.1 | 32.25 | 35.75 | 46.65 | 58.9 | 70.4 | 79.1 | 83.95 | 81.65 | 73.65 | 62.5 | 50.5 | 37.05 | 16.95 | 19.25 | 28.35 | 38.5 | 48.8 | 57.9 | 63.45 | 61.55 | 52.95 | 41.9 | 33.3 | 21.95
HELENA | MT | 19.6 | 26.4 | 33.6 | 43.4 | 52.5 | 62.1 | 69.2 | 67.4 | 55.4 | 45.1 | 31.6 | 21.2 | -17.1 | 18.1 | 19.9 | 21.5 | 23.5 | 24.2 | 25 | 29 | 30 | 27 | 24.3 | 18.9 | 17.6 | 28.65 | 36.35 | 44.35 | 55.15 | 64.6 | 74.6 | 83.7 | 82.4 | 68.9 | 57.25 | 41.05 | 30 | 10.55 | 16.45 | 22.85 | 31.65 | 40.4 | 49.6 | 54.7 | 52.4 | 41.9 | 32.95 | 22.15 | 12.4
HOUSTON | TX | 50.4 | 53.9 | 60.6 | 68.3 | 74.5 | 80.4 | 82.6 | 82.3 | 78.2 | 69.6 | 61 | 53.5 | 27.7 | 18.9 | 18.7 | 19.6 | 19.4 | 18 | 17.4 | 18.3 | 19.1 | 19.4 | 20 | 19.6 | 18.9 | 59.85 | 63.25 | 70.4 | 78 | 83.5 | 89.1 | 91.75 | 91.85 | 87.9 | 79.6 | 70.8 | 62.95 | 40.95 | 44.55 | 50.8 | 58.6 | 65.5 | 71.7 | 73.45 | 72.75 | 68.5 | 59.6 | 51.2 | 44.05
INDIANAPOLIS | IN | 25.5 | 29.6 | 41.4 | 52.4 | 62.8 | 71.9 | 75.4 | 73.2 | 66.6 | 54.7 | 43 | 30.9 | -1.8 | 14.4 | 15.6 | 17.8 | 19.6 | 19.3 | 18.8 | 18.4 | 18.5 | 20.3 | 19.5 | 16 | 13.8 | 32.7 | 37.4 | 50.3 | 62.2 | 72.45 | 81.3 | 84.6 | 82.45 | 76.75 | 64.45 | 51 | 37.8 | 18.3 | 21.8 | 32.5 | 42.6 | 53.15 | 62.5 | 66.2 | 63.95 | 56.45 | 44.95 | 35 | 24
JACKSON | MS | 44.1 | 47.9 | 56.7 | 64.6 | 72 | 78.8 | 81.5 | 80.9 | 75.9 | 64.7 | 55.8 | 47.8 | 21.1 | 20.3 | 20.9 | 22.2 | 22.8 | 20.9 | 20.1 | 19.3 | 20.1 | 21.4 | 23.4 | 22.4 | 20.4 | 54.25 | 58.35 | 67.8 | 76 | 82.45 | 88.85 | 91.15 | 90.95 | 86.6 | 76.4 | 67 | 58 | 33.95 | 37.45 | 45.6 | 53.2 | 61.55 | 68.75 | 71.85 | 70.85 | 65.2 | 53 | 44.6 | 37.6
JACKSONVILLE | FL | 52.4 | 55.2 | 61.1 | 67 | 73.4 | 79.1 | 81.6 | 81.2 | 78.1 | 69.8 | 61.9 | 55.1 | 28.6 | 21.7 | 21.5 | 22 | 22.7 | 21.4 | 18.2 | 18 | 17 | 15.9 | 18.5 | 20.7 | 21 | 63.25 | 65.95 | 72.1 | 78.35 | 84.1 | 88.2 | 90.6 | 89.7 | 86.05 | 79.05 | 72.25 | 65.6 | 41.55 | 44.45 | 50.1 | 55.65 | 62.7 | 70 | 72.6 | 72.7 | 70.15 | 60.55 | 51.55 | 44.6
KANSAS CITY | MO | 25.7 | 31.2 | 42.7 | 54.5 | 64.1 | 73.2 | 78.5 | 76.1 | 67.5 | 56.6 | 43.1 | 30.4 | -2.1 | 17 | 18.1 | 20.2 | 20.1 | 19.3 | 18.8 | 19 | 19.4 | 20.5 | 19.8 | 17.5 | 16.2 | 34.2 | 40.25 | 52.8 | 64.55 | 73.75 | 82.6 | 88 | 85.8 | 77.75 | 66.5 | 51.85 | 38.5 | 17.2 | 22.15 | 32.6 | 44.45 | 54.45 | 63.8 | 69 | 66.4 | 57.25 | 46.7 | 34.35 | 22.3
KNOXVILLE | TN | 36 | 40.1 | 49 | 57.5 | 65.4 | 73.2 | 76.6 | 76 | 70.1 | 58.4 | 48.7 | 40.1 | 14.2 | 17.1 | 18.7 | 21.1 | 21.8 | 20.9 | 19.6 | 18.7 | 19 | 20.3 | 21.6 | 20.1 | 17.4 | 44.55 | 49.45 | 59.55 | 68.4 | 75.85 | 83 | 85.95 | 85.5 | 80.25 | 69.2 | 58.75 | 48.8 | 27.45 | 30.75 | 38.45 | 46.6 | 54.95 | 63.4 | 67.25 | 66.5 | 59.95 | 47.6 | 38.65 | 31.4
LA CROSSE | WI | 14.4 | 19.9 | 32.8 | 47.7 | 59.5 | 68.5 | 73.5 | 70.8 | 61.8 | 50.2 | 35.6 | 20.3 | -13.7 | 15.7 | 16.4 | 17.3 | 20.1 | 20.5 | 20.8 | 20 | 19.3 | 19.6 | 18.7 | 14.5 | 13.8 | 22.25 | 28.1 | 41.45 | 57.75 | 69.75 | 78.9 | 83.5 | 80.45 | 71.6 | 59.55 | 42.85 | 27.2 | 6.55 | 11.7 | 24.15 | 37.65 | 49.25 | 58.1 | 63.5 | 61.15 | 52 | 40.85 | 28.35 | 13.4
LAS VEGAS | NV | 45.5 | 51.1 | 56.3 | 64.1 | 74 | 84.9 | 91.1 | 88.7 | 80.5 | 68.3 | 55 | 45.7 | 28.9 | 19.1 | 19.5 | 21.2 | 22.4 | 23.4 | 24.5 | 23.5 | 22.7 | 23.2 | 22.5 | 20.2 | 18.6 | 55.05 | 60.85 | 66.9 | 75.3 | 85.7 | 97.15 | 102.85 | 100.05 | 92.1 | 79.55 | 65.1 | 55 | 35.95 | 41.35 | 45.7 | 52.9 | 62.3 | 72.65 | 79.35 | 77.35 | 68.9 | 57.05 | 44.9 | 36.4
LEXINGTON | KY | 30.8 | 34.5 | 45.3 | 54.8 | 64 | 72.2 | 75.8 | 74.7 | 68.2 | 56.7 | 46 | 35.9 | 4.5 | 15.1 | 16.5 | 18.6 | 19.7 | 18.8 | 18.7 | 18.4 | 19 | 19.5 | 19.3 | 16.6 | 14.8 | 38.35 | 42.75 | 54.6 | 64.65 | 73.4 | 81.55 | 85 | 84.2 | 77.95 | 66.35 | 54.3 | 43.3 | 23.25 | 26.25 | 36 | 44.95 | 54.6 | 62.85 | 66.6 | 65.2 | 58.45 | 47.05 | 37.7 | 28.5
LITTLE ROCK | AR | 39.1 | 43.6 | 53.1 | 62.1 | 70.2 | 78.4 | 81.9 | 80.6 | 74.1 | 63 | 52.1 | 42.8 | 16.9 | 17.7 | 18.7 | 19.7 | 20.8 | 19.7 | 19.2 | 19 | 20 | 20.6 | 21.4 | 18.8 | 17.2 | 47.95 | 52.95 | 62.95 | 72.5 | 80.05 | 88 | 91.4 | 90.6 | 84.4 | 73.7 | 61.5 | 51.4 | 30.25 | 34.25 | 43.25 | 51.7 | 60.35 | 68.8 | 72.4 | 70.6 | 63.8 | 52.3 | 42.7 | 34.2
LOS ANGELES | CA | 56.8 | 57.6 | 58 | 60.1 | 62.7 | 65.7 | 69.1 | 70.5 | 69.9 | 66.8 | 61.6 | 56.9 | 43.9 | 15.3 | 13.9 | 12.3 | 12.6 | 10.8 | 10.3 | 10.4 | 10.7 | 11.4 | 12.8 | 15.4 | 15.8 | 64.45 | 64.55 | 64.15 | 66.4 | 68.1 | 70.85 | 74.3 | 75.85 | 75.6 | 73.2 | 69.3 | 64.8 | 49.15 | 50.65 | 51.85 | 53.8 | 57.3 | 60.55 | 63.9 | 65.15 | 64.2 | 60.4 | 53.9 | 49
LOUISVILLE | KY | 31.7 | 35.7 | 46.3 | 56.3 | 65.3 | 73.2 | 77.2 | 75.8 | 69.5 | 57.6 | 47.1 | 36.9 | 6.7 | 15.1 | 16.5 | 18.5 | 19.9 | 18.7 | 17.9 | 17.5 | 18 | 19.1 | 19.5 | 16.7 | 14.4 | 39.25 | 43.95 | 55.55 | 66.25 | 74.65 | 82.15 | 85.95 | 84.8 | 79.05 | 67.35 | 55.45 | 44.1 | 24.15 | 27.45 | 37.05 | 46.35 | 55.95 | 64.25 | 68.45 | 66.8 | 59.95 | 47.85 | 38.75 | 29.7
MEMPHIS | TN | 39.7 | 44.2 | 53.1 | 62.9 | 71.2 | 79.1 | 82.6 | 81 | 74.2 | 63.1 | 52.5 | 43.7 | 16.8 | 16.1 | 17 | 18.4 | 18.8 | 17.8 | 17.3 | 16.6 | 17.3 | 18.8 | 19.5 | 17.5 | 15.8 | 47.75 | 52.7 | 62.3 | 72.3 | 80.1 | 87.75 | 90.9 | 89.65 | 83.6 | 72.85 | 61.25 | 51.6 | 31.65 | 35.7 | 43.9 | 53.5 | 62.3 | 70.45 | 74.3 | 72.35 | 64.8 | 53.35 | 43.75 | 35.8
MIAMI | FL | 67.2 | 68.5 | 71.7 | 75.2 | 78.7 | 81.4 | 82.6 | 82.8 | 81.9 | 78.3 | 73.6 | 69.1 | 46.3 | 14.9 | 14.5 | 14 | 13.9 | 12.7 | 12 | 12.1 | 12.2 | 11.4 | 11.5 | 12 | 13.4 | 74.65 | 75.75 | 78.7 | 82.15 | 85.05 | 87.4 | 88.65 | 88.9 | 87.6 | 84.05 | 79.6 | 75.8 | 59.75 | 61.25 | 64.7 | 68.25 | 72.35 | 75.4 | 76.55 | 76.7 | 76.2 | 72.55 | 67.6 | 62.4
MILWAUKEE | WI | 18.9 | 23 | 33.3 | 44.4 | 54.6 | 65 | 70.9 | 69.3 | 61.7 | 50.3 | 37.7 | 24.4 | -5.2 | 12.9 | 12.7 | 13.9 | 15.7 | 17.1 | 17.2 | 15.6 | 14.4 | 15.7 | 15.4 | 13.2 | 12 | 25.35 | 29.35 | 40.25 | 52.25 | 63.15 | 73.6 | 78.7 | 76.5 | 69.55 | 58 | 44.3 | 30.4 | 12.45 | 16.65 | 26.35 | 36.55 | 46.05 | 56.4 | 63.1 | 62.1 | 53.85 | 42.6 | 31.1 | 18.4
MINNEAPOLIS | MN | 11.8 | 17.9 | 31 | 46.4 | 58.5 | 68.2 | 73.6 | 70.5 | 60.5 | 48.8 | 33.2 | 17.9 | -14.9 | 15 | 14.9 | 15.5 | 19.2 | 18.8 | 18.7 | 17.9 | 17.5 | 18 | 17.3 | 13.7 | 13.9 | 19.3 | 25.35 | 38.75 | 56 | 67.9 | 77.55 | 82.55 | 79.25 | 69.5 | 57.45 | 40.05 | 24.85 | 4.3 | 10.45 | 23.25 | 36.8 | 49.1 | 58.85 | 64.65 | 61.75 | 51.5 | 40.15 | 26.35 | 10.95
MOBILE | AL | 49.9 | 53.2 | 60.5 | 67.8 | 74.5 | 80.4 | 82.3 | 81.8 | 77.9 | 68.4 | 59.8 | 53 | 26.5 | 19.4 | 19.3 | 20.4 | 20.5 | 19.5 | 17.3 | 16.9 | 16.9 | 17.7 | 20 | 20.3 | 19.3 | 59.6 | 62.85 | 70.7 | 78.05 | 84.25 | 89.05 | 90.75 | 90.25 | 86.75 | 78.4 | 69.95 | 62.65 | 40.2 | 43.55 | 50.3 | 57.55 | 64.75 | 71.75 | 73.85 | 73.35 | 69.05 | 58.4 | 49.65 | 43.35
MONCTON | NEW BRUNSWICK | 17.06 | 18.68 | 28.04 | 39.02 | 51.26 | 60.8 | 66.92 | 65.48 | 56.84 | 46.04 | 35.78 | 23.18 | -9.2 | 17 | 17.2 | 16 | 15.9 | 19.5 | 19.9 | 19.1 | 19.2 | 19.1 | 16.8 | 13.6 | 15.1 | 25.56 | 27.28 | 36.04 | 46.97 | 61.01 | 70.75 | 76.47 | 75.08 | 66.39 | 54.44 | 42.58 | 30.73 | 8.56 | 10.08 | 20.04 | 31.07 | 41.51 | 50.85 | 57.37 | 55.88 | 47.29 | 37.64 | 28.98 | 15.63
MONTGOMERY | AL | 46.1 | 49.8 | 57.2 | 64.7 | 71.9 | 78.7 | 81.3 | 80.6 | 76.5 | 65.8 | 56.6 | 49.5 | 23.7 | 20.8 | 21.1 | 23 | 23.8 | 22.2 | 20.3 | 19.6 | 20 | 20.9 | 23.8 | 23.4 | 21.2 | 56.5 | 60.35 | 68.7 | 76.6 | 83 | 88.85 | 91.1 | 90.6 | 86.95 | 77.7 | 68.3 | 60.1 | 35.7 | 39.25 | 45.7 | 52.8 | 60.8 | 68.55 | 71.5 | 70.6 | 66.05 | 53.9 | 44.9 | 38.9
MONTREAL | QUEBEC | 13.64 | 16.88 | 27.86 | 42.26 | 56.12 | 64.76 | 69.62 | 67.28 | 58.28 | 46.58 | 34.88 | 20.66 | -11.2 | 14.3 | 15 | 14.7 | 16.8 | 17.8 | 17.5 | 16.8 | 16.9 | 16.7 | 14.7 | 12.3 | 12.9 | 20.79 | 24.38 | 35.21 | 50.66 | 65.02 | 73.51 | 78.02 | 75.73 | 66.63 | 53.93 | 41.03 | 27.11 | 6.49 | 9.38 | 20.51 | 33.86 | 47.22 | 56.01 | 61.22 | 58.83 | 49.93 | 39.23 | 28.73 | 14.21
NASHVILLE | TN | 36.2 | 40.4 | 50.2 | 59.2 | 67.7 | 75.6 | 79.3 | 78.1 | 71.8 | 60.4 | 50 | 40.5 | 11.6 | 17.4 | 18.7 | 20.5 | 21.3 | 19.9 | 18.9 | 18.4 | 19 | 20.1 | 21.2 | 19 | 17.1 | 44.9 | 49.75 | 60.45 | 69.85 | 77.65 | 85.05 | 88.5 | 87.6 | 81.85 | 71 | 59.5 | 49.05 | 27.5 | 31.05 | 39.95 | 48.55 | 57.75 | 66.15 | 70.1 | 68.6 | 61.75 | 49.8 | 40.5 | 31.95
NEW ORLEANS | LA | 51.3 | 54.3 | 61.6 | 68.5 | 74.8 | 80 | 81.9 | 81.5 | 78.1 | 69.1 | 61.1 | 54.5 | 30.6 | 16.8 | 16.6 | 17.5 | 17.7 | 16.7 | 15.3 | 15.3 | 15.4 | 14.9 | 16.7 | 17.3 | 16.8 | 59.7 | 62.6 | 70.35 | 77.35 | 83.15 | 87.65 | 89.55 | 89.2 | 85.55 | 77.45 | 69.75 | 62.9 | 42.9 | 46 | 52.85 | 59.65 | 66.45 | 72.35 | 74.25 | 73.8 | 70.65 | 60.75 | 52.45 | 46.1
NEW YORK CITY | NY | 31.5 | 33.6 | 42.4 | 52.5 | 62.7 | 71.6 | 76.8 | 75.5 | 68.2 | 57.5 | 47.6 | 36.6 | 13.1 | 12 | 12.7 | 13.8 | 14.4 | 14.4 | 14.1 | 13.4 | 12.9 | 13.5 | 13.7 | 12.7 | 11.7 | 37.5 | 39.95 | 49.3 | 59.7 | 69.9 | 78.65 | 83.5 | 81.95 | 74.95 | 64.35 | 53.95 | 42.45 | 25.5 | 27.25 | 35.5 | 45.3 | 55.5 | 64.55 | 70.1 | 69.05 | 61.45 | 50.65 | 41.25 | 30.75
NORFOLK | VA | 39.1 | 41 | 48.6 | 57 | 66.1 | 74.1 | 78.2 | 77.2 | 71.9 | 61.2 | 52.5 | 43.8 | 20.4 | 14.9 | 15.5 | 16.9 | 17.8 | 16.7 | 15.5 | 14.5 | 13.7 | 13.3 | 15.2 | 16.3 | 15.3 | 46.55 | 48.75 | 57.05 | 65.9 | 74.45 | 81.85 | 85.45 | 84.05 | 78.55 | 68.8 | 60.65 | 51.45 | 31.65 | 33.25 | 40.15 | 48.1 | 57.75 | 66.35 | 70.95 | 70.35 | 65.25 | 53.6 | 44.35 | 36.15
OKLAHOMA CITY | OK | 35.9 | 40.9 | 50.3 | 60.4 | 68.4 | 76.7 | 82 | 81.1 | 73 | 62 | 49.6 | 39.3 | 10.3 | 19.7 | 20.5 | 21 | 21.4 | 19.5 | 19.4 | 21 | 21.3 | 20.7 | 20.7 | 20 | 18.7 | 45.75 | 51.15 | 60.8 | 71.1 | 78.15 | 86.4 | 92.5 | 91.75 | 83.35 | 72.35 | 59.6 | 48.65 | 26.05 | 30.65 | 39.8 | 49.7 | 58.65 | 67 | 71.5 | 70.45 | 62.65 | 51.65 | 39.6 | 29.95
OMAHA | NE | 20.5 | 25.9 | 37.7 | 51.4 | 62.4 | 71.9 | 76.5 | 73.9 | 64.8 | 53.6 | 38.7 | 24.4 | -8.1 | 18.3 | 18.5 | 21.1 | 22.2 | 21.2 | 20.7 | 19.8 | 19.7 | 22.3 | 22 | 18.6 | 17.2 | 29.65 | 35.15 | 48.25 | 62.5 | 73 | 82.25 | 86.4 | 83.75 | 75.95 | 64.6 | 48 | 33 | 11.35 | 16.65 | 27.15 | 40.3 | 51.8 | 61.55 | 66.6 | 64.05 | 53.65 | 42.6 | 29.4 | 15.8
OTTAWA | ONTARIO | 12.56 | 16.34 | 27.5 | 42.26 | 56.12 | 64.94 | 69.62 | 67.1 | 57.74 | 46.04 | 33.8 | 19.22 | -12 | 14.8 | 15.7 | 15.5 | 17.3 | 18.6 | 18.4 | 18.3 | 18 | 17.7 | 15.5 | 12.6 | 13 | 19.96 | 24.19 | 35.25 | 50.91 | 65.42 | 74.14 | 78.77 | 76.1 | 66.59 | 53.79 | 40.1 | 25.72 | 5.16 | 8.49 | 19.75 | 33.61 | 46.82 | 55.74 | 60.47 | 58.1 | 48.89 | 38.29 | 27.5 | 12.72
PHILADELPHIA | PA | 30.4 | 33 | 42.4 | 52.4 | 62.9 | 71.8 | 76.7 | 75.5 | 68.2 | 56.4 | 46.4 | 35.8 | 11.6 | 13.8 | 15.1 | 17.1 | 18.7 | 18.7 | 18 | 16.9 | 16.3 | 16.6 | 17.1 | 15.9 | 13.7 | 37.3 | 40.55 | 50.95 | 61.75 | 72.25 | 80.8 | 85.15 | 83.65 | 76.5 | 64.95 | 54.35 | 42.65 | 23.5 | 25.45 | 33.85 | 43.05 | 53.55 | 62.8 | 68.25 | 67.35 | 59.9 | 47.85 | 38.45 | 28.95
PHOENIX | AZ | 53.6 | 57.7 | 62.2 | 69.9 | 78.8 | 88.2 | 93.5 | 91.5 | 85.6 | 74.5 | 61.9 | 54.1 | 37.2 | 20.8 | 20.9 | 22.3 | 23.8 | 24.5 | 25.1 | 21.6 | 20.4 | 21.6 | 22.5 | 21.6 | 20.2 | 64 | 68.15 | 73.35 | 81.8 | 91.05 | 100.75 | 104.3 | 101.7 | 96.4 | 85.75 | 72.7 | 64.2 | 43.2 | 47.25 | 51.05 | 58 | 66.55 | 75.65 | 82.7 | 81.3 | 74.8 | 63.25 | 51.1 | 44
PITTSBURG | PA | 26.1 | 28.7 | 39.4 | 49.6 | 59.5 | 67.9 | 72.1 | 70.5 | 63.9 | 52.4 | 42.3 | 31.5 | 1.8 | 14 | 15.6 | 18.2 | 20.4 | 20 | 19.6 | 18.5 | 18.8 | 19.1 | 18.7 | 15.5 | 13.5 | 33.1 | 36.5 | 48.5 | 59.8 | 69.5 | 77.7 | 81.35 | 79.9 | 73.45 | 61.75 | 50.05 | 38.25 | 19.1 | 20.9 | 30.3 | 39.4 | 49.5 | 58.1 | 62.85 | 61.1 | 54.35 | 43.05 | 34.55 | 24.75
PORTLAND - ME | ME | 20.8 | 23.3 | 33 | 43.3 | 53.3 | 62.4 | 68.6 | 67.3 | 59.1 | 48.5 | 38.7 | 26.5 | -1.6 | 16.2 | 16.8 | 15.8 | 16.8 | 17.4 | 18.1 | 18 | 17.9 | 18 | 18.2 | 15.7 | 15.6 | 28.9 | 31.7 | 40.9 | 51.7 | 62 | 71.45 | 77.6 | 76.25 | 68.1 | 57.6 | 46.55 | 34.3 | 12.7 | 14.9 | 25.1 | 34.9 | 44.6 | 53.35 | 59.6 | 58.35 | 50.1 | 39.4 | 30.85 | 18.7
PORTLAND - OR | OR | 39.6 | 43.6 | 47.3 | 51 | 57.1 | 63.5 | 68.2 | 68.6 | 63.3 | 54.5 | 46.1 | 40.2 | 21.9 | 9.9 | 13.6 | 15.7 | 16.8 | 17.9 | 18.9 | 21.3 | 22 | 21.4 | 16.4 | 10.8 | 9.2 | 44.55 | 50.4 | 55.15 | 59.4 | 66.05 | 72.95 | 78.85 | 79.6 | 74 | 62.7 | 51.5 | 44.8 | 34.65 | 36.8 | 39.45 | 42.6 | 48.15 | 54.05 | 57.55 | 57.6 | 52.6 | 46.3 | 40.7 | 35.6
PROVIDENCE | RI | 27.9 | 29.7 | 37.4 | 47.4 | 57.3 | 66.9 | 72.7 | 71.3 | 64.1 | 53.6 | 44 | 32.8 | 6.1 | 15.2 | 15.4 | 16.4 | 17.5 | 18.3 | 17.9 | 17.2 | 16.6 | 17.3 | 18 | 16.3 | 15 | 35.5 | 37.4 | 45.6 | 56.15 | 66.45 | 75.85 | 81.3 | 79.6 | 72.75 | 62.6 | 52.15 | 40.3 | 20.3 | 22 | 29.2 | 38.65 | 48.15 | 57.95 | 64.1 | 63 | 55.45 | 44.6 | 35.85 | 25.3
RALEIGH | NC | 38.9 | 42 | 50.4 | 59 | 67 | 74.3 | 78.1 | 77.1 | 71.1 | 60.1 | 51.2 | 42.6 | 16.3 | 18.6 | 19.9 | 21.9 | 23 | 21.7 | 19.8 | 18.9 | 18.5 | 18.8 | 21.5 | 21.5 | 19.2 | 48.2 | 51.95 | 61.35 | 70.5 | 77.85 | 84.2 | 87.55 | 86.35 | 80.5 | 70.85 | 61.95 | 52.2 | 29.6 | 32.05 | 39.45 | 47.5 | 56.15 | 64.4 | 68.65 | 67.85 | 61.7 | 49.35 | 40.45 | 33
REGINA | SASKATCHEWAN | 2.84 | 10.58 | 23 | 40.1 | 53.06 | 61.52 | 65.84 | 64.4 | 53.06 | 40.64 | 22.1 | 8.24 | -29.3 | 17.8 | 17.5 | 16.8 | 22.6 | 23.9 | 21.9 | 23 | 24.6 | 24.1 | 22.8 | 17.5 | 17.4 | 11.74 | 19.33 | 31.4 | 51.4 | 65.01 | 72.47 | 77.34 | 76.7 | 65.11 | 52.04 | 30.85 | 16.94 | -6.06 | 1.83 | 14.6 | 28.8 | 41.11 | 50.57 | 54.34 | 52.1 | 41.01 | 29.24 | 13.35 | -0.46
RENO | NV | 32.9 | 38 | 42.8 | 48.6 | 56.5 | 65.1 | 71.6 | 69.6 | 60.4 | 50.8 | 40.3 | 32.7 | 8.8 | 20.5 | 22.7 | 24.5 | 26.1 | 28.1 | 31.1 | 33.9 | 34.3 | 33.3 | 30.9 | 24.7 | 20.7 | 43.15 | 49.35 | 55.05 | 61.65 | 70.55 | 80.65 | 88.55 | 86.75 | 77.05 | 66.25 | 52.65 | 43.05 | 22.65 | 26.65 | 30.55 | 35.55 | 42.45 | 49.55 | 54.65 | 52.45 | 43.75 | 35.35 | 27.95 | 22.35
ROANOKE | VA | 34.5 | 37.3 | 46.8 | 55.6 | 64.1 | 71.5 | 75.6 | 74.6 | 67.7 | 56.5 | 47.5 | 38.3 | 12.7 | 16.7 | 18 | 19.8 | 21 | 20.8 | 19.6 | 19.1 | 19.1 | 19.4 | 20.9 | 19.4 | 16.6 | 42.85 | 46.3 | 56.7 | 66.1 | 74.5 | 81.3 | 85.15 | 84.15 | 77.4 | 66.95 | 57.2 | 46.6 | 26.15 | 28.3 | 36.9 | 45.1 | 53.7 | 61.7 | 66.05 | 65.05 | 58 | 46.05 | 37.8 | 30
SACRAMENTO | CA | 45.2 | 50.7 | 53.6 | 58.3 | 65.3 | 71.6 | 75.7 | 75.1 | 71.5 | 64.2 | 53.3 | 45.3 | 31.1 | 13.6 | 17.9 | 20 | 24.5 | 26.4 | 29.3 | 32.1 | 31.8 | 30.8 | 27.8 | 20.7 | 15.4 | 52 | 59.65 | 63.6 | 70.55 | 78.5 | 86.25 | 91.75 | 91 | 86.9 | 78.1 | 63.65 | 53 | 38.4 | 41.75 | 43.6 | 46.05 | 52.1 | 56.95 | 59.65 | 59.2 | 56.1 | 50.3 | 42.95 | 37.6
SAINT JOHN'S | NEWFOUNDLAND | 17.42 | 18.86 | 27.5 | 38.48 | 48.92 | 57.2 | 62.78 | 62.42 | 55.04 | 45.14 | 35.6 | 23.54 | 3 | 12.1 | 12.4 | 11.4 | 11.5 | 15 | 15.7 | 15.3 | 14 | 13.2 | 11 | 10.6 | 10.5 | 23.47 | 25.06 | 33.2 | 44.23 | 56.42 | 65.05 | 70.43 | 69.42 | 61.64 | 50.64 | 40.9 | 28.79 | 11.37 | 12.66 | 21.8 | 32.73 | 41.42 | 49.35 | 55.13 | 55.42 | 48.44 | 39.64 | 30.3 | 18.29
SALT LAKE CITY | UT | 27.9 | 34.1 | 41.8 | 49.7 | 58.8 | 69.1 | 77.9 | 75.6 | 65.2 | 53.2 | 40.8 | 29.7 | 7 | 14.3 | 16.2 | 18.6 | 20.4 | 22.5 | 24.8 | 25.9 | 25 | 24 | 22 | 17.2 | 13.9 | 35.05 | 42.2 | 51.1 | 59.9 | 70.05 | 81.5 | 90.85 | 88.1 | 77.2 | 64.2 | 49.4 | 36.65 | 20.75 | 26 | 32.5 | 39.5 | 47.55 | 56.7 | 64.95 | 63.1 | 53.2 | 42.2 | 32.2 | 22.75
SAN ANTONIO | TX | 49.3 | 53.5 | 61.7 | 69.3 | 75.5 | 82.2 | 85 | 84.9 | 79.3 | 70.2 | 60.4 | 52.2 | 26.7 | 20.7 | 20.8 | 21 | 21.1 | 18.9 | 18.7 | 19.1 | 20.1 | 20.1 | 20.4 | 20.3 | 20.5 | 59.65 | 63.9 | 72.2 | 79.85 | 84.95 | 91.55 | 94.55 | 94.95 | 89.35 | 80.4 | 70.55 | 62.45 | 38.95 | 43.1 | 51.2 | 58.75 | 66.05 | 72.85 | 75.45 | 74.85 | 69.25 | 60 | 50.25 | 41.95
SAN DIEGO | CA | 57.4 | 58.6 | 59.6 | 62 | 64.1 | 66.8 | 71 | 72.6 | 71.4 | 67.7 | 62 | 57.4 | 44.8 | 18.9 | 16.7 | 14.4 | 14.6 | 12.5 | 11.7 | 13.4 | 14.1 | 14.4 | 15.4 | 18.7 | 20.4 | 66.85 | 66.95 | 66.8 | 69.3 | 70.35 | 72.65 | 77.7 | 79.65 | 78.6 | 75.4 | 71.35 | 67.6 | 47.95 | 50.25 | 52.4 | 54.7 | 57.85 | 60.95 | 64.3 | 65.55 | 64.2 | 60 | 52.65 | 47.2
SAN FRANCISCO | CA | 48.7 | 52.2 | 53.3 | 55.6 | 58.1 | 61.5 | 62.7 | 63.7 | 64.5 | 61 | 54.8 | 49.4 | 37.8 | 10.9 | 12.2 | 13 | 14.4 | 14.7 | 15.6 | 15.7 | 15.4 | 16.7 | 16 | 13 | 11 | 54.15 | 58.3 | 59.8 | 62.8 | 65.45 | 69.3 | 70.55 | 71.4 | 72.85 | 69 | 61.3 | 54.9 | 43.25 | 46.1 | 46.8 | 48.4 | 50.75 | 53.7 | 54.85 | 56 | 56.15 | 53 | 48.3 | 43.9
SAVANNAH | GA | 48.9 | 51.8 | 59.2 | 66 | 73.5 | 79.1 | 81.8 | 81 | 76.6 | 67.3 | 59.1 | 51.7 | 26.2 | 20.3 | 20.6 | 21.2 | 22.2 | 21 | 18.2 | 18.1 | 16.9 | 16.5 | 19.2 | 20.9 | 20.3 | 59.05 | 62.1 | 69.8 | 77.1 | 84 | 88.2 | 90.85 | 89.45 | 84.85 | 76.9 | 69.55 | 61.85 | 38.75 | 41.5 | 48.6 | 54.9 | 63 | 70 | 72.75 | 72.55 | 68.35 | 57.7 | 48.65 | 41.55
SEATTLE | WA | 41.3 | 44.3 | 46.6 | 50.4 | 56.1 | 61.4 | 65.3 | 65.7 | 60.8 | 53.5 | 46.3 | 41.6 | 23.9 | 8.7 | 11.5 | 12.9 | 14.6 | 15.6 | 16.5 | 18.5 | 18.8 | 16.9 | 12.3 | 9.4 | 8.6 | 45.65 | 50.05 | 53.05 | 57.7 | 63.9 | 69.65 | 74.55 | 75.1 | 69.25 | 59.65 | 51 | 45.9 | 36.95 | 38.55 | 40.15 | 43.1 | 48.3 | 53.15 | 56.05 | 56.3 | 52.35 | 47.35 | 41.6 | 37.3
SHREVEPORT | LA | 45.1 | 49.3 | 57.5 | 65.6 | 72.6 | 79.4 | 82.7 | 82.2 | 76.7 | 66.5 | 56.7 | 48 | 22.7 | 19.2 | 19.7 | 21 | 21.5 | 19.3 | 18.8 | 19.2 | 20.4 | 20.9 | 21.4 | 20.1 | 18.9 | 54.7 | 59.15 | 68 | 76.35 | 82.25 | 88.8 | 92.3 | 92.4 | 87.15 | 77.2 | 66.75 | 57.45 | 35.5 | 39.45 | 47 | 54.85 | 62.95 | 70 | 73.1 | 72 | 66.25 | 55.8 | 46.65 | 38.55
SIOUX FALLS | SD | 13.8 | 19.7 | 32.5 | 46.9 | 58.4 | 68.3 | 74.3 | 71.4 | 60.9 | 48.6 | 33 | 18.3 | -15.2 | 18 | 18 | 18.8 | 22.4 | 21.6 | 21.2 | 20.7 | 20.8 | 22.2 | 22.3 | 18 | 17.4 | 22.8 | 28.7 | 41.9 | 58.1 | 69.2 | 78.9 | 84.65 | 81.8 | 72 | 59.75 | 42 | 27 | 4.8 | 10.7 | 23.1 | 35.7 | 47.6 | 57.7 | 63.95 | 61 | 49.8 | 37.45 | 24 | 9.6
SYRACUSE | NY | 24 | 26.1 | 34.1 | 46.5 | 57.6 | 66.6 | 71.4 | 69.7 | 61.9 | 50.6 | 40.8 | 29.8 | -2.7 | 14.9 | 15.9 | 17 | 19 | 20.7 | 20.2 | 19.4 | 19.2 | 19.2 | 17.8 | 14.4 | 13.3 | 31.45 | 34.05 | 42.6 | 56 | 67.95 | 76.7 | 81.1 | 79.3 | 71.5 | 59.5 | 48 | 36.45 | 16.55 | 18.15 | 25.6 | 37 | 47.25 | 56.5 | 61.7 | 60.1 | 52.3 | 41.7 | 33.6 | 23.15
SPOKANE | WA | 27.1 | 33.3 | 38.7 | 45.9 | 53.9 | 62 | 68.8 | 68.4 | 58.9 | 47.3 | 35.1 | 27.8 | 0.8 | 9.6 | 13.5 | 17.2 | 20.1 | 22.1 | 23 | 26.3 | 26.6 | 25 | 20.7 | 11.8 | 9.7 | 31.9 | 40.05 | 47.3 | 55.95 | 64.95 | 73.5 | 81.95 | 81.7 | 71.4 | 57.65 | 41 | 32.65 | 22.3 | 26.55 | 30.1 | 35.85 | 42.85 | 50.5 | 55.65 | 55.1 | 46.4 | 36.95 | 29.2 | 22.95
SPRINGFIELD | IL | 24.2 | 28.7 | 40.8 | 53.2 | 63.5 | 72.9 | 76.5 | 73.7 | 67.3 | 55.6 | 42.9 | 29.7 | -3.3 | 14.7 | 15.7 | 18 | 20.4 | 20.4 | 19.6 | 19.3 | 19.6 | 22.5 | 20.8 | 16.6 | 14.5 | 31.55 | 36.55 | 49.8 | 63.4 | 73.7 | 82.7 | 86.15 | 83.5 | 78.55 | 66 | 51.2 | 36.95 | 16.85 | 20.85 | 31.8 | 43 | 53.3 | 63.1 | 66.85 | 63.9 | 56.05 | 45.2 | 34.6 | 22.45
ST. LOUIS | MO | 29.3 | 33.9 | 45.1 | 56.7 | 66.1 | 75.4 | 79.8 | 77.6 | 70.2 | 58.4 | 46.2 | 33.9 | 2 | 15 | 16.5 | 18 | 19 | 18.1 | 17.3 | 17.1 | 17.3 | 18.6 | 18.4 | 16.1 | 14.6 | 36.8 | 42.15 | 54.1 | 66.2 | 75.15 | 84.05 | 88.35 | 86.25 | 79.5 | 67.6 | 54.25 | 41.2 | 21.8 | 25.65 | 36.1 | 47.2 | 57.05 | 66.75 | 71.25 | 68.95 | 60.9 | 49.2 | 38.15 | 26.6
TALLAHASSEE | FL | 50.5 | 53.2 | 60.2 | 66.3 | 73.6 | 79.6 | 81.3 | 81.3 | 78.3 | 68.7 | 59.7 | 53.2 | 24.9 | 23.5 | 24 | 25.1 | 26.3 | 24.3 | 20.1 | 19.1 | 18.7 | 19.2 | 23 | 23.8 | 23.2 | 62.25 | 65.2 | 72.75 | 79.45 | 85.75 | 89.65 | 90.85 | 90.65 | 87.9 | 80.2 | 71.6 | 64.8 | 38.75 | 41.2 | 47.65 | 53.15 | 61.45 | 69.55 | 71.75 | 71.95 | 68.7 | 57.2 | 47.8 | 41.6
TAMPA | FL | 59.9 | 61.5 | 66.6 | 71.3 | 77.4 | 81.3 | 82.4 | 82.4 | 80.9 | 74.8 | 67.5 | 62.2 | 36.6 | 18.2 | 17.9 | 17.9 | 17.9 | 17.5 | 14.8 | 14.3 | 14.2 | 14.5 | 16.2 | 17.3 | 17.7 | 69 | 70.45 | 75.55 | 80.25 | 86.15 | 88.7 | 89.55 | 89.5 | 88.15 | 82.9 | 76.15 | 71.05 | 50.8 | 52.55 | 57.65 | 62.35 | 68.65 | 73.9 | 75.25 | 75.3 | 73.65 | 66.7 | 58.85 | 53.35
TORONTO | ONTARIO | 20.66 | 22.28 | 31.28 | 43.34 | 55.22 | 64.04 | 69.44 | 67.82 | 59.54 | 48.02 | 37.76 | 26.78 | 4.6 | 13 | 13.6 | 14.8 | 16.7 | 18.4 | 18.5 | 18.3 | 17.9 | 17.8 | 15.8 | 12.4 | 11.7 | 27.16 | 29.08 | 38.68 | 51.69 | 64.42 | 73.29 | 78.59 | 76.77 | 68.44 | 55.92 | 43.96 | 32.63 | 14.16 | 15.48 | 23.88 | 34.99 | 46.02 | 54.79 | 60.29 | 58.87 | 50.64 | 40.12 | 31.56 | 20.93
TRENTON | NJ | 30.9 | 33 | 41.5 | 50 | 60.4 | 69.4 | 74.7 | 73.4 | 66.1 | 54.9 | 45.8 | 35.8 | 8.6 | 15 | 16.2 | 19 | 19.7 | 19.6 | 18.9 | 18.9 | 18 | 19.3 | 19.7 | 18.2 | 15.1 | 38.4 | 41.1 | 51 | 59.85 | 70.2 | 78.85 | 84.15 | 82.4 | 75.75 | 64.75 | 54.9 | 43.35 | 23.4 | 24.9 | 32 | 40.15 | 50.6 | 59.95 | 65.25 | 64.4 | 56.45 | 45.05 | 36.7 | 28.25
TUCSON | AZ
VANCOUVER | BRITISH COLUMBIA | 37.94 | 40.64 | 43.88 | 48.56 | 54.5 | 59.36 | 63.5 | 63.68 | 58.28 | 50.18 | 42.8 | 38.3 | 19.4 | 8.8 | 10.6 | 11.2 | 12.3 | 12.7 | 12.9 | 13.7 | 13.7 | 13 | 10.4 | 9 | 8.6 | 42.34 | 45.94 | 49.48 | 54.71 | 60.85 | 65.81 | 70.35 | 70.53 | 64.78 | 55.38 | 47.3 | 42.6 | 33.54 | 35.34 | 38.28 | 42.41 | 48.15 | 52.91 | 56.65 | 56.83 | 51.78 | 44.98 | 38.3 | 34
WASHINGTON DC | DC | 34.6 | 37.5 | 47.2 | 56.5 | 66.4 | 75.6 | 80 | 78.5 | 71.3 | 59.7 | 49.8 | 39.4 | 15.9 | 17.2 | 18.7 | 20.8 | 22.9 | 22.1 | 21.2 | 20.5 | 20.5 | 21.2 | 22.8 | 20.7 | 17.6 | 43.2 | 46.85 | 57.6 | 67.95 | 77.45 | 86.2 | 90.25 | 88.75 | 81.9 | 71.1 | 60.15 | 48.2 | 26 | 28.15 | 36.8 | 45.05 | 55.35 | 65 | 69.75 | 68.25 | 60.7 | 48.3 | 39.45 | 30.6
WICHITA | KS | 29.5 | 34.8 | 45.4 | 56.4 | 65.6 | 75.7 | 81.4 | 79.3 | 70.3 | 58.6 | 44.7 | 33 | 2.6 | 19.1 | 20.7 | 21.6 | 21.6 | 20.3 | 20.8 | 21.8 | 21.4 | 21.9 | 21.5 | 20 | 18.1 | 39.05 | 45.15 | 56.2 | 67.2 | 75.75 | 86.1 | 92.3 | 90 | 81.25 | 69.35 | 54.7 | 42.05 | 19.95 | 24.45 | 34.6 | 45.6 | 55.45 | 65.3 | 70.5 | 68.6 | 59.35 | 47.85 | 34.7 | 23.95
WINNIPEG | MANITOBA | -0.04 | 7.52 | 21.02 | 39.2 | 53.6 | 62.6 | 67.1 | 65.3 | 54.14 | 41.54 | 22.46 | 6.08 | -26 | 16.3 | 16.8 | 16.3 | 21.1 | 23.4 | 20.5 | 20.5 | 21.9 | 20.9 | 18.3 | 14.3 | 15.3 | 8.11 | 15.92 | 29.17 | 49.75 | 65.3 | 72.85 | 77.35 | 76.25 | 64.59 | 50.69 | 29.61 | 13.73 | -8.19 | -0.88 | 12.87 | 28.65 | 41.9 | 52.35 | 56.85 | 54.35 | 43.69 | 32.39 | 15.31 | -1.57
WORCESTER | MA | 22.8 | 24.8 | 33.7 | 44.4 | 55.5 | 64.2 | 69.7 | 68 | 60.2 | 50 | 39.4 | 27.4 | 1.4 | 13.9 | 14.4 | 15.6 | 17.1 | 18 | 17 | 16.2 | 156 | 15.5 | 15.6 | 14 | 13.6 | 29.75 | 32 | 41.5 | 52.95 | 64.5 | 72.7 | 77.8 | 146 | 67.95 | 57.8 | 46.4 | 34.2 | 15.85 | 17.6 | 25.9 | 35.85 | 46.5 | 55.7 | 61.6 | -10 | 52.45 | 42.2 | 32.4 | 20.6

## HOURLY TEMP CALC (hidden)
| Average Hourly Temperature For Selected City: | [16 empty] | SYRACUSE
[6 empty] | h: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
|  | Avg | Range | Max | Min | F(t): | 0.87 | 0.92 | 0.96 | 0.99 | 1 | 0.98 | 0.93 | 0.84 | 0.71 | 0.56 | 0.39 | 0.23 | 0.11 | 0.03 | 0 | 0.03 | 0.1 | 0.21 | 0.34 | 0.47 | 0.58 | 0.68 | 0.76 | 0.82
3 | JAN | 24 | 14.9 | 31.45 | 16.55 |  | 18.487 | 17.742 | 17.146 | 16.699 | 16.55 | 16.848 | 17.593 | 18.934 | 20.871 | 23.106 | 25.639 | 28.023 | 29.811 | 31.003 | 31.45 | 31.003 | 29.96 | 28.321 | 26.384 | 24.447 | 22.808 | 21.318 | 20.126 | 19.232
4 | FEB | 26 | 15.9 | 33.95 | 18.05 |  | 20.117 | 19.322 | 18.686 | 18.209 | 18.05 | 18.368 | 19.163 | 20.594 | 22.661 | 25.046 | 27.749 | 30.293 | 32.201 | 33.473 | 33.95 | 33.473 | 32.36 | 30.611 | 28.544 | 26.477 | 24.728 | 23.138 | 21.866 | 20.912
5 | MAR | 34 | 17 | 42.5 | 25.5 |  | 27.71 | 26.86 | 26.18 | 25.67 | 25.5 | 25.84 | 26.69 | 28.22 | 30.43 | 32.98 | 35.87 | 38.59 | 40.63 | 41.99 | 42.5 | 41.99 | 40.8 | 38.93 | 36.72 | 34.51 | 32.64 | 30.94 | 29.58 | 28.56
6 | APR | 47 | 19 | 56.5 | 37.5 |  | 39.97 | 39.02 | 38.26 | 37.69 | 37.5 | 37.88 | 38.83 | 40.54 | 43.01 | 45.86 | 49.09 | 52.13 | 54.41 | 55.93 | 56.5 | 55.93 | 54.6 | 52.51 | 50.04 | 47.57 | 45.48 | 43.58 | 42.06 | 40.92
7 | MAY | 58 | 20.7 | 68.35 | 47.65 |  | 50.341 | 49.306 | 48.478 | 47.857 | 47.65 | 48.064 | 49.099 | 50.962 | 53.653 | 56.758 | 60.277 | 63.589 | 66.073 | 67.729 | 68.35 | 67.729 | 66.28 | 64.003 | 61.312 | 58.621 | 56.344 | 54.274 | 52.618 | 51.376
8 | JUN | 67 | 20.2 | 77.1 | 56.9 |  | 59.526 | 58.516 | 57.708 | 57.102 | 56.9 | 57.304 | 58.314 | 60.132 | 62.758 | 65.788 | 69.222 | 72.454 | 74.878 | 76.494 | 77.1 | 76.494 | 75.08 | 72.858 | 70.232 | 67.606 | 65.384 | 63.364 | 61.748 | 60.536
9 | JUL | 71 | 19.4 | 80.7 | 61.3 |  | 63.822 | 62.852 | 62.076 | 61.494 | 61.3 | 61.688 | 62.658 | 64.404 | 66.926 | 69.836 | 73.134 | 76.238 | 78.566 | 80.118 | 80.7 | 80.118 | 78.76 | 76.626 | 74.104 | 71.582 | 69.448 | 67.508 | 65.956 | 64.792
10 | AUG | 70 | 19.2 | 79.6 | 60.4 |  | 62.896 | 61.936 | 61.168 | 60.592 | 60.4 | 60.784 | 61.744 | 63.472 | 65.968 | 68.848 | 72.112 | 75.184 | 77.488 | 79.024 | 79.6 | 79.024 | 77.68 | 75.568 | 73.072 | 70.576 | 68.464 | 66.544 | 65.008 | 63.856
11 | SEP | 62 | 19.2 | 71.6 | 52.4 |  | 54.896 | 53.936 | 53.168 | 52.592 | 52.4 | 52.784 | 53.744 | 55.472 | 57.968 | 60.848 | 64.112 | 67.184 | 69.488 | 71.024 | 71.6 | 71.024 | 69.68 | 67.568 | 65.072 | 62.576 | 60.464 | 58.544 | 57.008 | 55.856
12 | OCT | 51 | 17.8 | 59.9 | 42.1 |  | 44.414 | 43.524 | 42.812 | 42.278 | 42.1 | 42.456 | 43.346 | 44.948 | 47.262 | 49.932 | 52.958 | 55.806 | 57.942 | 59.366 | 59.9 | 59.366 | 58.12 | 56.162 | 53.848 | 51.534 | 49.576 | 47.796 | 46.372 | 45.304
13 | NOV | 41 | 14.4 | 48.2 | 33.8 |  | 35.672 | 34.952 | 34.376 | 33.944 | 33.8 | 34.088 | 34.808 | 36.104 | 37.976 | 40.136 | 42.584 | 44.888 | 46.616 | 47.768 | 48.2 | 47.768 | 46.76 | 45.176 | 43.304 | 41.432 | 39.848 | 38.408 | 37.256 | 36.392
14 | DEC | 30 | 13.3 | 36.65 | 23.35 |  | 25.079 | 24.414 | 23.882 | 23.483 | 23.35 | 23.616 | 24.281 | 25.478 | 27.207 | 29.202 | 31.463 | 33.591 | 35.187 | 36.251 | 36.65 | 36.251 | 35.32 | 33.857 | 32.128 | 30.399 | 28.936 | 27.606 | 26.542 | 25.744

## BTU REQUIREMENTS (hidden)
BTU Requirements For Selected City: | [16 empty] | SYRACUSE
Month: |  |  | JAN |  |  |  | Number of Boilers Choosen: |  |  | 4 |  | Average Monthly Efficiency: |  |  | 92.5% |  | Total BTU For Month: |  |  | 6219336062.1758 |  |  |  |  | Month | Total Load | Total BTU Input | Avg Efficiency
[25 empty] | JAN | 5743068493.1507 | 6219336062.1758 | 92.5%
Day Hours | [24 empty] | FEB | 4975561643.8356 | 5358700752.7547 | 93.06%
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | MAR | 4509863013.6986 | 4737823459.2296 | 95.54%
Hourly Temperature °F | [24 empty] | APR | 2850410958.9041 | 2897562885.8908 | 98.62%
| 18 | 18 | 17 | 17 | 17 | 17 | 18 | 19 | 21 | 23 | 26 | 28 | 30 | 31 | 31 | 31 | 30 | 28 | 26 | 24 | 23 | 21 | 20 | 19 | MAY | 1498191780.8219 | 1506266681.6645 | 99.51%
Outlet Water Temperature °F | [24 empty] | JUN | 616438356.1644 | 618293235.872 | 0.997
| 144 | 144 | 145 | 145 | 145 | 145 | 144 | 142 | 139 | 137 | 132 | 129 | 126 | 125 | 125 | 125 | 126 | 129 | 132 | 135 | 137 | 139 | 141 | 142 | JUL | 244602739.726 | 245338755.994 | 99.7%
Return Water Temperature °F | [24 empty] | AUG | 341424657.5342 | 342452013.575 | 99.7%
| 124 | 124 | 125 | 125 | 125 | 125 | 124 | 122 | 119 | 117 | 112 | 109 | 106 | 105 | 105 | 105 | 106 | 109 | 112 | 115 | 117 | 119 | 121 | 122 | SEP | 1020821917.8082 | 1023893598.604 | 99.7%
Efficiency at Current Inlet Water Temperature (20% Fire) | [24 empty] | OCT | 2466410958.9041 | 2493163072.5361 | 99.11%
| 0.92231 | 0.92231 | 0.92042 | 0.92042 | 0.92042 | 0.92042 | 0.92231 | 0.9261 | 0.93188 | 0.93565 | 0.94507 | 0.95072 | 0.95637 | 0.95825 | 0.95825 | 0.95825 | 0.95637 | 0.95072 | 0.94507 | 0.93942 | 0.93565 | 0.93188 | 0.92799 | 0.9261 | NOV | 3540821917.8082 | 3632476906.0522 | 97.66%
Efficiency at Current Inlet Water Temperature (40% Fire) | [24 empty] | DEC | 5004164383.5616 | 5317964851.4599 | 94.32%
| 0.91798 | 0.91798 | 0.91617 | 0.91617 | 0.91617 | 0.91617 | 0.91798 | 0.9216 | 0.92683 | 0.9305 | 0.93967 | 0.94517 | 0.95067 | 0.9525 | 0.9525 | 0.9525 | 0.95067 | 0.94517 | 0.93967 | 0.93417 | 0.9305 | 0.92683 | 0.92341 | 0.9216
Efficiency at Current Inlet Water Temperature (60% Fire)
| 0.91211 | 0.91211 | 0.91042 | 0.91042 | 0.91042 | 0.91042 | 0.91211 | 0.9155 | 0.91978 | 0.92335 | 0.93227 | 0.93762 | 0.94297 | 0.94475 | 0.94475 | 0.94475 | 0.94297 | 0.93762 | 0.93227 | 0.92692 | 0.92335 | 0.91978 | 0.91719 | 0.9155
Efficiency at Current Inlet Water Temperature (80% Fire)
| 0.90489 | 0.90489 | 0.90333 | 0.90333 | 0.90333 | 0.90333 | 0.90489 | 0.908 | 0.91077 | 0.9143 | 0.92313 | 0.92843 | 0.93373 | 0.9355 | 0.9355 | 0.9355 | 0.93373 | 0.92843 | 0.92313 | 0.91783 | 0.9143 | 0.91077 | 0.90956 | 0.908
Efficiency at Current Inlet Water Temperature (100% Fire)
| 0.8974 | 0.8974 | 0.896 | 0.896 | 0.896 | 0.896 | 0.8974 | 0.9002 | 0.9017 | 0.9051 | 0.9136 | 0.9187 | 0.9238 | 0.9255 | 0.9255 | 0.9255 | 0.9238 | 0.9187 | 0.9136 | 0.9085 | 0.9051 | 0.9017 | 0.9016 | 0.9002
Building Load (BTU/hr)
| 8547945.2055 | 8547945.2055 | 8712328.7671 | 8712328.7671 | 8712328.7671 | 8712328.7671 | 8547945.2055 | 8383561.6438 | 8054794.5205 | 7726027.3973 | 7232876.7123 | 6904109.589 | 6575342.4658 | 6410958.9041 | 6410958.9041 | 6410958.9041 | 6575342.4658 | 6904109.589 | 7232876.7123 | 7561643.8356 | 7726027.3973 | 8054794.5205 | 8219178.0822 | 8383561.6438
All Boilers Ouput At 20% Fire (BTU/hr)
| 2951395.5556 | 2951395.5556 | 2945333.3333 | 2945333.3333 | 2945333.3333 | 2945333.3333 | 2951395.5556 | 2963520 | 2982026.6667 | 2994080 | 3024213.3333 | 3042293.3333 | 3060373.3333 | 3066400 | 3066400 | 3066400 | 3060373.3333 | 3042293.3333 | 3024213.3333 | 3006133.3333 | 2994080 | 2982026.6667 | 2969582.2222 | 2963520
All Boilers Ouput At 40% Fire (BTU/hr)
| 5875057.7778 | 5875057.7778 | 5863466.6667 | 5863466.6667 | 5863466.6667 | 5863466.6667 | 5875057.7778 | 5898240 | 5931733.3333 | 5955200 | 6013866.6667 | 6049066.6667 | 6084266.6667 | 6096000 | 6096000 | 6096000 | 6084266.6667 | 6049066.6667 | 6013866.6667 | 5978666.6667 | 5955200 | 5931733.3333 | 5909831.1111 | 5898240
All Boilers Ouput At 60% Fire (BTU/hr)
| 8756266.6667 | 8756266.6667 | 8740000 | 8740000 | 8740000 | 8740000 | 8756266.6667 | 8788800 | 8829920 | 8864160 | 8949760 | 9001120 | 9052480 | 9069600 | 9069600 | 9069600 | 9052480 | 9001120 | 8949760 | 8898400 | 8864160 | 8829920 | 8805066.6667 | 8788800
All Boilers Ouput At 80% Fire (BTU/hr)
| 11582577.7778 | 11582577.7778 | 11562666.6667 | 11562666.6667 | 11562666.6667 | 11562666.6667 | 11582577.7778 | 11622400 | 11657813.3333 | 11703040 | 11816106.6667 | 11883946.6667 | 11951786.6667 | 11974400 | 11974400 | 11974400 | 11951786.6667 | 11883946.6667 | 11816106.6667 | 11748266.6667 | 11703040 | 11657813.3333 | 11642311.1111 | 11622400
All Boilers Ouput At 100% Fire (BTU/hr)
| 12922560 | 12922560 | 12902400 | 12902400 | 12902400 | 12902400 | 12922560 | 12962880 | 12984480 | 13033440 | 13155840 | 13229280 | 13302720 | 13327200 | 13327200 | 13327200 | 13302720 | 13229280 | 13155840 | 13082400 | 13033440 | 12984480 | 12983040 | 12962880
Hourly system efficiency
| 0.91211 | 0.91211 | 0.91042 | 0.91042 | 0.91042 | 0.91042 | 0.91211 | 0.9155 | 0.91978 | 0.92335 | 0.93227 | 0.93762 | 0.94297 | 0.94475 | 0.94475 | 0.94475 | 0.94297 | 0.93762 | 0.93227 | 0.92692 | 0.92335 | 0.91978 | 0.91719 | 0.9155
Boiler Gas Consumption (BTU/hr)
| 9371605.1711 | 9371605.1711 | 9569605.9685 | 9569605.9685 | 9569605.9685 | 9569605.9685 | 9371605.1711 | 9157358.4313 | 8757273.8368 | 8367387.6615 | 7758377.4803 | 7363467.2191 | 6973038.0704 | 6785878.7024 | 6785878.7024 | 6785878.7024 | 6973038.0704 | 7363467.2191 | 7758377.4803 | 8157846.4468 | 8367387.6615 | 8757273.8368 | 8961216.6013 | 9157358.4313
Month: |  |  | FEB |  |  |  | Number of Boilers Choosen: |  |  | 4 |  | Average Monthly Efficiency: |  |  | 93.06% |  | Total BTU For Month: |  |  | 5358700752.7547
Day Hours
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Hourly Temperature °F
| 20 | 19 | 19 | 18 | 18 | 18 | 19 | 21 | 23 | 25 | 28 | 30 | 32 | 33 | 34 | 33 | 32 | 31 | 29 | 26 | 25 | 23 | 22 | 21
Outlet Water Temperature °F
| 141 | 142 | 142 | 144 | 144 | 144 | 142 | 139 | 137 | 134 | 129 | 126 | 123 | 122 | 121 | 122 | 123 | 125 | 128 | 132 | 134 | 137 | 138 | 139
Return Water Temperature °F
| 121 | 122 | 122 | 124 | 124 | 124 | 122 | 119 | 117 | 114 | 109 | 106 | 103 | 102 | 101 | 102 | 103 | 105 | 108 | 112 | 114 | 117 | 118 | 119
Efficiency at Current Inlet Water Temperature (20% Fire)
| 0.92799 | 0.9261 | 0.9261 | 0.92231 | 0.92231 | 0.92231 | 0.9261 | 0.93188 | 0.93565 | 0.9413 | 0.95072 | 0.95637 | 0.96202 | 0.9639 | 0.96578 | 0.9639 | 0.96202 | 0.95825 | 0.9526 | 0.94507 | 0.9413 | 0.93565 | 0.93377 | 0.93188
Efficiency at Current Inlet Water Temperature (40% Fire)
| 0.92341 | 0.9216 | 0.9216 | 0.91798 | 0.91798 | 0.91798 | 0.9216 | 0.92683 | 0.9305 | 0.936 | 0.94517 | 0.95067 | 0.95617 | 0.958 | 0.95983 | 0.958 | 0.95617 | 0.9525 | 0.947 | 0.93967 | 0.936 | 0.9305 | 0.92867 | 0.92683
Efficiency at Current Inlet Water Temperature (60% Fire)
| 0.91719 | 0.9155 | 0.9155 | 0.91211 | 0.91211 | 0.91211 | 0.9155 | 0.91978 | 0.92335 | 0.9287 | 0.93762 | 0.94297 | 0.94832 | 0.9501 | 0.95188 | 0.9501 | 0.94832 | 0.94475 | 0.9394 | 0.93227 | 0.9287 | 0.92335 | 0.92157 | 0.91978
Efficiency at Current Inlet Water Temperature (80% Fire)
| 0.90956 | 0.908 | 0.908 | 0.90489 | 0.90489 | 0.90489 | 0.908 | 0.91077 | 0.9143 | 0.9196 | 0.92843 | 0.93373 | 0.93903 | 0.9408 | 0.94257 | 0.9408 | 0.93903 | 0.9355 | 0.9302 | 0.92313 | 0.9196 | 0.9143 | 0.91253 | 0.91077
Efficiency at Current Inlet Water Temperature (100% Fire)
| 0.9016 | 0.9002 | 0.9002 | 0.8974 | 0.8974 | 0.8974 | 0.9002 | 0.9017 | 0.9051 | 0.9102 | 0.9187 | 0.9238 | 0.9289 | 0.9306 | 0.9323 | 0.9306 | 0.9289 | 0.9255 | 0.9204 | 0.9136 | 0.9102 | 0.9051 | 0.9034 | 0.9017
Building Load (BTU/hr)
| 8219178.0822 | 8383561.6438 | 8383561.6438 | 8547945.2055 | 8547945.2055 | 8547945.2055 | 8383561.6438 | 8054794.5205 | 7726027.3973 | 7397260.274 | 6904109.589 | 6575342.4658 | 6246575.3425 | 6082191.7808 | 5917808.2192 | 6082191.7808 | 6246575.3425 | 6410958.9041 | 6739726.0274 | 7232876.7123 | 7397260.274 | 7726027.3973 | 7890410.9589 | 8054794.5205
All Boilers Ouput At 20% Fire (BTU/hr)
| 2969582.2222 | 2963520 | 2963520 | 2951395.5556 | 2951395.5556 | 2951395.5556 | 2963520 | 2982026.6667 | 2994080 | 3012160 | 3042293.3333 | 3060373.3333 | 3078453.3333 | 3084480 | 3090506.6667 | 3084480 | 3078453.3333 | 3066400 | 3048320 | 3024213.3333 | 3012160 | 2994080 | 2988053.3333 | 2982026.6667
All Boilers Ouput At 40% Fire (BTU/hr)
| 5909831.1111 | 5898240 | 5898240 | 5875057.7778 | 5875057.7778 | 5875057.7778 | 5898240 | 5931733.3333 | 5955200 | 5990400 | 6049066.6667 | 6084266.6667 | 6119466.6667 | 6131200 | 6142933.3333 | 6131200 | 6119466.6667 | 6096000 | 6060800 | 6013866.6667 | 5990400 | 5955200 | 5943466.6667 | 5931733.3333
All Boilers Ouput At 60% Fire (BTU/hr)
| 8805066.6667 | 8788800 | 8788800 | 8756266.6667 | 8756266.6667 | 8756266.6667 | 8788800 | 8829920 | 8864160 | 8915520 | 9001120 | 9052480 | 9103840 | 9120960 | 9138080 | 9120960 | 9103840 | 9069600 | 9018240 | 8949760 | 8915520 | 8864160 | 8847040 | 8829920
All Boilers Ouput At 80% Fire (BTU/hr)
| 11642311.1111 | 11622400 | 11622400 | 11582577.7778 | 11582577.7778 | 11582577.7778 | 11622400 | 11657813.3333 | 11703040 | 11770880 | 11883946.6667 | 11951786.6667 | 12019626.6667 | 12042240 | 12064853.3333 | 12042240 | 12019626.6667 | 11974400 | 11906560 | 11816106.6667 | 11770880 | 11703040 | 11680426.6667 | 11657813.3333
All Boilers Ouput At 100% Fire (BTU/hr)
| 12983040 | 12962880 | 12962880 | 12922560 | 12922560 | 12922560 | 12962880 | 12984480 | 13033440 | 13106880 | 13229280 | 13302720 | 13376160 | 13400640 | 13425120 | 13400640 | 13376160 | 13327200 | 13253760 | 13155840 | 13106880 | 13033440 | 13008960 | 12984480
Hourly system efficiency
| 0.91719 | 0.9155 | 0.9155 | 0.91211 | 0.91211 | 0.91211 | 0.9155 | 0.91978 | 0.92335 | 0.9287 | 0.93762 | 0.94297 | 0.94832 | 0.958 | 0.95983 | 0.958 | 0.94832 | 0.94475 | 0.9394 | 0.93227 | 0.9287 | 0.92335 | 0.92157 | 0.91978
Boiler Gas Consumption (BTU/hr)
| 8961216.6013 | 9157358.4313 | 9157358.4313 | 9371605.1711 | 9371605.1711 | 9371605.1711 | 9157358.4313 | 8757273.8368 | 8367387.6615 | 7965177.4243 | 7363467.2191 | 6973038.0704 | 6587014.1927 | 6348843.195 | 6165453.953 | 6348843.195 | 6587014.1927 | 6785878.7024 | 7174500.7743 | 7758377.4803 | 7965177.4243 | 8367387.6615 | 8561953.5128 | 8757273.8368
Month: |  |  | MAR |  |  |  | Number of Boilers Choosen: |  |  | 4 |  | Average Monthly Efficiency: |  |  | 95.54% |  | Total BTU For Month: |  |  | 4737823459.2296
Day Hours
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Hourly Temperature °F
| 28 | 27 | 26 | 26 | 26 | 26 | 27 | 28 | 30 | 33 | 36 | 39 | 41 | 42 | 43 | 42 | 41 | 39 | 37 | 35 | 33 | 31 | 30 | 29
Outlet Water Temperature °F
| 129 | 131 | 132 | 132 | 132 | 132 | 131 | 129 | 126 | 122 | 118 | 113 | 110 | 109 | 107 | 109 | 110 | 113 | 116 | 119 | 122 | 125 | 126 | 128
Return Water Temperature °F
| 109 | 111 | 112 | 112 | 112 | 112 | 111 | 109 | 106 | 102 | 98 | 93 | 90 | 89 | 87 | 89 | 90 | 93 | 96 | 99 | 102 | 105 | 106 | 108
Efficiency at Current Inlet Water Temperature (20% Fire)
| 0.95072 | 0.94695 | 0.94507 | 0.94507 | 0.94507 | 0.94507 | 0.94695 | 0.95072 | 0.95637 | 0.9639 | 0.9773 | 0.98305 | 0.9865 | 0.98765 | 0.98995 | 0.98765 | 0.9865 | 0.98305 | 0.9796 | 0.97615 | 0.9639 | 0.95825 | 0.95637 | 0.9526
Efficiency at Current Inlet Water Temperature (40% Fire)
| 0.94517 | 0.9415 | 0.93967 | 0.93967 | 0.93967 | 0.93967 | 0.9415 | 0.94517 | 0.95067 | 0.958 | 0.9704 | 0.9764 | 0.98 | 0.9812 | 0.9836 | 0.9812 | 0.98 | 0.9764 | 0.9728 | 0.9692 | 0.958 | 0.9525 | 0.95067 | 0.947
Efficiency at Current Inlet Water Temperature (60% Fire)
| 0.93762 | 0.93405 | 0.93227 | 0.93227 | 0.93227 | 0.93227 | 0.93405 | 0.93762 | 0.94297 | 0.9501 | 0.9615 | 0.96775 | 0.9715 | 0.97275 | 0.97525 | 0.97275 | 0.9715 | 0.96775 | 0.964 | 0.96025 | 0.9501 | 0.94475 | 0.94297 | 0.9394
Efficiency at Current Inlet Water Temperature (80% Fire)
| 0.92843 | 0.9249 | 0.92313 | 0.92313 | 0.92313 | 0.92313 | 0.9249 | 0.92843 | 0.93373 | 0.9408 | 0.9492 | 0.9572 | 0.962 | 0.9636 | 0.9668 | 0.9636 | 0.962 | 0.9572 | 0.9524 | 0.9476 | 0.9408 | 0.9355 | 0.93373 | 0.9302
Efficiency at Current Inlet Water Temperature (100% Fire)
| 0.9187 | 0.9153 | 0.9136 | 0.9136 | 0.9136 | 0.9136 | 0.9153 | 0.9187 | 0.9238 | 0.9306 | 0.9366 | 0.9456 | 0.951 | 0.9528 | 0.9564 | 0.9528 | 0.951 | 0.9456 | 0.9402 | 0.9348 | 0.9306 | 0.9255 | 0.9238 | 0.9204
Building Load (BTU/hr)
| 6904109.589 | 7068493.1507 | 7232876.7123 | 7232876.7123 | 7232876.7123 | 7232876.7123 | 7068493.1507 | 6904109.589 | 6575342.4658 | 6082191.7808 | 5589041.0959 | 5095890.411 | 4767123.2877 | 4602739.726 | 4438356.1644 | 4602739.726 | 4767123.2877 | 5095890.411 | 5424657.5342 | 5753424.6575 | 6082191.7808 | 6410958.9041 | 6575342.4658 | 6739726.0274
All Boilers Ouput At 20% Fire (BTU/hr)
| 3042293.3333 | 3030240 | 3024213.3333 | 3024213.3333 | 3024213.3333 | 3024213.3333 | 3030240 | 3042293.3333 | 3060373.3333 | 3084480 | 3127360 | 3145760 | 3156800 | 3160480 | 3167840 | 3160480 | 3156800 | 3145760 | 3134720 | 3123680 | 3084480 | 3066400 | 3060373.3333 | 3048320
All Boilers Ouput At 40% Fire (BTU/hr)
| 6049066.6667 | 6025600 | 6013866.6667 | 6013866.6667 | 6013866.6667 | 6013866.6667 | 6025600 | 6049066.6667 | 6084266.6667 | 6131200 | 6210560 | 6248960 | 6272000 | 6279680 | 6295040 | 6279680 | 6272000 | 6248960 | 6225920 | 6202880 | 6131200 | 6096000 | 6084266.6667 | 6060800
All Boilers Ouput At 60% Fire (BTU/hr)
| 9001120 | 8966880 | 8949760 | 8949760 | 8949760 | 8949760 | 8966880 | 9001120 | 9052480 | 9120960 | 9230400 | 9290400 | 9326400 | 9338400 | 9362400 | 9338400 | 9326400 | 9290400 | 9254400 | 9218400 | 9120960 | 9069600 | 9052480 | 9018240
All Boilers Ouput At 80% Fire (BTU/hr)
| 11883946.6667 | 11838720 | 11816106.6667 | 11816106.6667 | 11816106.6667 | 11816106.6667 | 11838720 | 11883946.6667 | 11951786.6667 | 12042240 | 12149760 | 12252160 | 12313600 | 12334080 | 12375040 | 12334080 | 12313600 | 12252160 | 12190720 | 12129280 | 12042240 | 11974400 | 11951786.6667 | 11906560
All Boilers Ouput At 100% Fire (BTU/hr)
| 13229280 | 13180320 | 13155840 | 13155840 | 13155840 | 13155840 | 13180320 | 13229280 | 13302720 | 13400640 | 13487040 | 13616640 | 13694400 | 13720320 | 13772160 | 13720320 | 13694400 | 13616640 | 13538880 | 13461120 | 13400640 | 13327200 | 13302720 | 13253760
Hourly system efficiency
| 0.93762 | 0.93405 | 0.93227 | 0.93227 | 0.93227 | 0.93227 | 0.93405 | 0.93762 | 0.94297 | 0.958 | 0.9704 | 0.9764 | 0.98 | 0.9812 | 0.9836 | 0.9812 | 0.98 | 0.9764 | 0.9728 | 0.9692 | 0.958 | 0.94475 | 0.94297 | 0.9394
Boiler Gas Consumption (BTU/hr)
| 7363467.2191 | 7567574.7023 | 7758377.4803 | 7758377.4803 | 7758377.4803 | 7758377.4803 | 7567574.7023 | 7363467.2191 | 6973038.0704 | 6348843.195 | 5759522.976 | 5219060.2324 | 4864411.518 | 4690929.1949 | 4512358.8495 | 4690929.1949 | 4864411.518 | 5219060.2324 | 5576333.814 | 5936261.5121 | 6348843.195 | 6785878.7024 | 6973038.0704 | 7174500.7743
Month: |  |  | APR |  |  |  | Number of Boilers Choosen: |  |  | 4 |  | Average Monthly Efficiency: |  |  | 98.62% |  | Total BTU For Month: |  |  | 2897562885.8908
Day Hours
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Hourly Temperature °F
| 40 | 39 | 38 | 38 | 38 | 38 | 39 | 41 | 43 | 46 | 49 | 52 | 54 | 56 | 57 | 56 | 55 | 53 | 50 | 48 | 45 | 44 | 42 | 41
Outlet Water Temperature °F
| 112 | 113 | 115 | 115 | 115 | 115 | 113 | 110 | 107 | 103 | 99 | 94 | 91 | 89 | 87 | 89 | 90 | 93 | 97 | 100 | 105 | 106 | 109 | 110
Return Water Temperature °F
| 92 | 93 | 95 | 95 | 95 | 95 | 93 | 90 | 87 | 83 | 79 | 74 | 71 | 69 | 67 | 69 | 70 | 73 | 77 | 80 | 85 | 86 | 89 | 90
Efficiency at Current Inlet Water Temperature (20% Fire)
| 0.9842 | 0.98305 | 0.98075 | 0.98075 | 0.98075 | 0.98075 | 0.98305 | 0.9865 | 0.98995 | 0.99455 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.998 | 0.99225 | 0.9911 | 0.98765 | 0.9865
Efficiency at Current Inlet Water Temperature (40% Fire)
| 0.9776 | 0.9764 | 0.974 | 0.974 | 0.974 | 0.974 | 0.9764 | 0.98 | 0.9836 | 0.9884 | 0.991 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.992 | 0.986 | 0.9848 | 0.9812 | 0.98
Efficiency at Current Inlet Water Temperature (60% Fire)
| 0.969 | 0.96775 | 0.96525 | 0.96525 | 0.96525 | 0.96525 | 0.96775 | 0.9715 | 0.97525 | 0.98025 | 0.984 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.984 | 0.97775 | 0.9765 | 0.97275 | 0.9715
Efficiency at Current Inlet Water Temperature (80% Fire)
| 0.9588 | 0.9572 | 0.954 | 0.954 | 0.954 | 0.954 | 0.9572 | 0.962 | 0.9668 | 0.9732 | 0.971 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.978 | 0.97 | 0.9684 | 0.9636 | 0.962
Efficiency at Current Inlet Water Temperature (100% Fire)
| 0.9474 | 0.9456 | 0.942 | 0.942 | 0.942 | 0.942 | 0.9456 | 0.951 | 0.9564 | 0.9636 | 0.958 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.969 | 0.96 | 0.9582 | 0.9528 | 0.951
Building Load (BTU/hr)
| 4931506.8493 | 5095890.411 | 5260273.9726 | 5260273.9726 | 5260273.9726 | 5260273.9726 | 5095890.411 | 4767123.2877 | 4438356.1644 | 3945205.4795 | 3452054.7945 | 2958904.1096 | 2630136.9863 | 2301369.863 | 2136986.3014 | 2301369.863 | 2465753.4247 | 2794520.5479 | 3287671.2329 | 3616438.3562 | 4109589.0411 | 4273972.6027 | 4602739.726 | 4767123.2877
All Boilers Ouput At 20% Fire (BTU/hr)
| 3149440 | 3145760 | 3138400 | 3138400 | 3138400 | 3138400 | 3145760 | 3156800 | 3167840 | 3182560 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3193600 | 3175200 | 3171520 | 3160480 | 3156800
All Boilers Ouput At 40% Fire (BTU/hr)
| 6256640 | 6248960 | 6233600 | 6233600 | 6233600 | 6233600 | 6248960 | 6272000 | 6295040 | 6325760 | 6342400 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6348800 | 6310400 | 6302720 | 6279680 | 6272000
All Boilers Ouput At 60% Fire (BTU/hr)
| 9302400 | 9290400 | 9266400 | 9266400 | 9266400 | 9266400 | 9290400 | 9326400 | 9362400 | 9410400 | 9446400 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9446400 | 9386400 | 9374400 | 9338400 | 9326400
All Boilers Ouput At 80% Fire (BTU/hr)
| 12272640 | 12252160 | 12211200 | 12211200 | 12211200 | 12211200 | 12252160 | 12313600 | 12375040 | 12456960 | 12428800 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12518400 | 12416000 | 12395520 | 12334080 | 12313600
All Boilers Ouput At 100% Fire (BTU/hr)
| 13642560 | 13616640 | 13564800 | 13564800 | 13564800 | 13564800 | 13616640 | 13694400 | 13772160 | 13875840 | 13795200 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 13953600 | 13824000 | 13798080 | 13720320 | 13694400
Hourly system efficiency
| 0.9776 | 0.9764 | 0.974 | 0.974 | 0.974 | 0.974 | 0.9764 | 0.98 | 0.9836 | 0.9884 | 0.991 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.992 | 0.986 | 0.9848 | 0.9812 | 0.98
Boiler Gas Consumption (BTU/hr)
| 5044503.7329 | 5219060.2324 | 5400691.9637 | 5400691.9637 | 5400691.9637 | 5400691.9637 | 5219060.2324 | 4864411.518 | 4512358.8495 | 3991506.9602 | 3483405.4435 | 2967807.5322 | 2638051.1397 | 2308294.7473 | 2143416.551 | 2308294.7473 | 2473172.9435 | 2802929.336 | 3297563.9247 | 3645603.1816 | 4167940.204 | 4339939.686 | 4690929.1949 | 4864411.518
Month: |  |  | MAY |  |  |  | Number of Boilers Choosen: |  |  | 4 |  | Average Monthly Efficiency: |  |  | 99.51% |  | Total BTU For Month: |  |  | 1506266681.6645
Day Hours
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Hourly Temperature °F
| 50 | 49 | 48 | 48 | 48 | 48 | 49 | 51 | 54 | 57 | 60 | 64 | 66 | 68 | 68 | 68 | 66 | 64 | 61 | 59 | 56 | 54 | 53 | 51
Outlet Water Temperature °F
| 97 | 99 | 100 | 100 | 100 | 100 | 99 | 96 | 91 | 87 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 84 | 89 | 91 | 93 | 96
Return Water Temperature °F
| 77 | 79 | 80 | 80 | 80 | 80 | 79 | 76 | 71 | 67 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 64 | 69 | 71 | 73 | 76
Efficiency at Current Inlet Water Temperature (20% Fire)
| 0.997 | 0.997 | 0.998 | 0.998 | 0.998 | 0.998 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (40% Fire)
| 0.997 | 0.991 | 0.992 | 0.992 | 0.992 | 0.992 | 0.991 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (60% Fire)
| 0.997 | 0.984 | 0.984 | 0.984 | 0.984 | 0.984 | 0.984 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (80% Fire)
| 0.997 | 0.971 | 0.978 | 0.978 | 0.978 | 0.978 | 0.971 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (100% Fire)
| 0.997 | 0.958 | 0.969 | 0.969 | 0.969 | 0.969 | 0.958 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Building Load (BTU/hr)
| 3287671.2329 | 3452054.7945 | 3616438.3562 | 3616438.3562 | 3616438.3562 | 3616438.3562 | 3452054.7945 | 3123287.6712 | 2630136.9863 | 2136986.3014 | 1643835.6164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1479452.0548 | 1808219.1781 | 2301369.863 | 2630136.9863 | 2794520.5479 | 3123287.6712
All Boilers Ouput At 20% Fire (BTU/hr)
| 3190400 | 3190400 | 3193600 | 3193600 | 3193600 | 3193600 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400
All Boilers Ouput At 40% Fire (BTU/hr)
| 6380800 | 6342400 | 6348800 | 6348800 | 6348800 | 6348800 | 6342400 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800
All Boilers Ouput At 60% Fire (BTU/hr)
| 9571200 | 9446400 | 9446400 | 9446400 | 9446400 | 9446400 | 9446400 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200
All Boilers Ouput At 80% Fire (BTU/hr)
| 12761600 | 12428800 | 12518400 | 12518400 | 12518400 | 12518400 | 12428800 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600
All Boilers Ouput At 100% Fire (BTU/hr)
| 14356800 | 13795200 | 13953600 | 13953600 | 13953600 | 13953600 | 13795200 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800
Hourly system efficiency
| 0.997 | 0.991 | 0.992 | 0.992 | 0.992 | 0.992 | 0.991 | 0.997 | 0.997 | 0.997 | 0.997 | [7 empty] | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Boiler Gas Consumption (BTU/hr)
| 3297563.9247 | 3483405.4435 | 3645603.1816 | 3645603.1816 | 3645603.1816 | 3645603.1816 | 3483405.4435 | 3132685.7284 | 2638051.1397 | 2143416.551 | 1648781.9623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1483903.7661 | 1813660.1586 | 2308294.7473 | 2638051.1397 | 2802929.336 | 3132685.7284
Month: |  |  | JUN |  |  |  | Number of Boilers Choosen: |  |  | 4 |  | Average Monthly Efficiency: |  |  | 99.7% |  | Total BTU For Month: |  |  | 618293235.872
Day Hours
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Hourly Temperature °F
| 60 | 59 | 58 | 57 | 57 | 57 | 58 | 60 | 63 | 66 | 69 | 72 | 75 | 76 | 77 | 76 | 75 | 73 | 70 | 68 | 65 | 63 | 62 | 61
Outlet Water Temperature °F
| 83 | 84 | 86 | 87 | 87 | 87 | 86 | 83 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 80 | 81
Return Water Temperature °F
| 63 | 64 | 66 | 67 | 67 | 67 | 66 | 63 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 60 | 61
Efficiency at Current Inlet Water Temperature (20% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (40% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (60% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (80% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (100% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Building Load (BTU/hr)
| 1643835.6164 | 1808219.1781 | 1972602.7397 | 2136986.3014 | 2136986.3014 | 2136986.3014 | 1972602.7397 | 1643835.6164 | 1150684.9315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150684.9315 | 1315068.4932 | 1479452.0548
All Boilers Ouput At 20% Fire (BTU/hr)
| 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400
All Boilers Ouput At 40% Fire (BTU/hr)
| 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800
All Boilers Ouput At 60% Fire (BTU/hr)
| 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200
All Boilers Ouput At 80% Fire (BTU/hr)
| 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600
All Boilers Ouput At 100% Fire (BTU/hr)
| 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800
Hourly system efficiency
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | [12 empty] | 0.997 | 0.997 | 0.997
Boiler Gas Consumption (BTU/hr)
| 1648781.9623 | 1813660.1586 | 1978538.3548 | 2143416.551 | 2143416.551 | 2143416.551 | 1978538.3548 | 1648781.9623 | 1154147.3736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1154147.3736 | 1319025.5699 | 1483903.7661
Month: |  |  | JUL |  |  |  | Number of Boilers Choosen: |  |  | 4 |  | Average Monthly Efficiency: |  |  | 99.7% |  | Total BTU For Month: |  |  | 245338755.994
Day Hours
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Hourly Temperature °F
| 64 | 63 | 62 | 61 | 61 | 62 | 63 | 64 | 67 | 70 | 73 | 76 | 79 | 80 | 81 | 80 | 79 | 77 | 74 | 72 | 69 | 68 | 66 | 65
Outlet Water Temperature °F
| 0 | 78 | 80 | 81 | 81 | 80 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Return Water Temperature °F
| 0 | 58 | 60 | 61 | 61 | 60 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Efficiency at Current Inlet Water Temperature (20% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (40% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (60% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (80% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (100% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Building Load (BTU/hr)
| 0 | 1150684.9315 | 1315068.4932 | 1479452.0548 | 1479452.0548 | 1315068.4932 | 1150684.9315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All Boilers Ouput At 20% Fire (BTU/hr)
| 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400
All Boilers Ouput At 40% Fire (BTU/hr)
| 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800
All Boilers Ouput At 60% Fire (BTU/hr)
| 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200
All Boilers Ouput At 80% Fire (BTU/hr)
| 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600
All Boilers Ouput At 100% Fire (BTU/hr)
| 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800
Hourly system efficiency
|  | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Boiler Gas Consumption (BTU/hr)
| 0 | 1154147.3736 | 1319025.5699 | 1483903.7661 | 1483903.7661 | 1319025.5699 | 1154147.3736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Month: |  |  | AUG |  |  |  | Number of Boilers Choosen: |  |  | 4 |  | Average Monthly Efficiency: |  |  | 99.7% |  | Total BTU For Month: |  |  | 342452013.575
Day Hours
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Hourly Temperature °F
| 63 | 62 | 61 | 61 | 60 | 61 | 62 | 63 | 66 | 69 | 72 | 75 | 77 | 79 | 80 | 79 | 78 | 76 | 73 | 71 | 68 | 67 | 65 | 64
Outlet Water Temperature °F
| 78 | 80 | 81 | 81 | 83 | 81 | 80 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Return Water Temperature °F
| 58 | 60 | 61 | 61 | 63 | 61 | 60 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Efficiency at Current Inlet Water Temperature (20% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (40% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (60% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (80% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (100% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Building Load (BTU/hr)
| 1150684.9315 | 1315068.4932 | 1479452.0548 | 1479452.0548 | 1643835.6164 | 1479452.0548 | 1315068.4932 | 1150684.9315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All Boilers Ouput At 20% Fire (BTU/hr)
| 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400
All Boilers Ouput At 40% Fire (BTU/hr)
| 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800
All Boilers Ouput At 60% Fire (BTU/hr)
| 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200
All Boilers Ouput At 80% Fire (BTU/hr)
| 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600
All Boilers Ouput At 100% Fire (BTU/hr)
| 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800
Hourly system efficiency
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Boiler Gas Consumption (BTU/hr)
| 1154147.3736 | 1319025.5699 | 1483903.7661 | 1483903.7661 | 1648781.9623 | 1483903.7661 | 1319025.5699 | 1154147.3736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Month: |  |  | SEP |  |  |  | Number of Boilers Choosen: |  |  | 4 |  | Average Monthly Efficiency: |  |  | 99.7% |  | Total BTU For Month: |  |  | 1023893598.604
Day Hours
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Hourly Temperature °F
| 55 | 54 | 53 | 53 | 52 | 53 | 54 | 55 | 58 | 61 | 64 | 67 | 69 | 71 | 72 | 71 | 70 | 68 | 65 | 63 | 60 | 59 | 57 | 56
Outlet Water Temperature °F
| 90 | 91 | 93 | 93 | 94 | 93 | 91 | 90 | 86 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 83 | 84 | 87 | 89
Return Water Temperature °F
| 70 | 71 | 73 | 73 | 74 | 73 | 71 | 70 | 66 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 63 | 64 | 67 | 69
Efficiency at Current Inlet Water Temperature (20% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (40% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (60% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (80% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Efficiency at Current Inlet Water Temperature (100% Fire)
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Building Load (BTU/hr)
| 2465753.4247 | 2630136.9863 | 2794520.5479 | 2794520.5479 | 2958904.1096 | 2794520.5479 | 2630136.9863 | 2465753.4247 | 1972602.7397 | 1479452.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150684.9315 | 1643835.6164 | 1808219.1781 | 2136986.3014 | 2301369.863
All Boilers Ouput At 20% Fire (BTU/hr)
| 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400
All Boilers Ouput At 40% Fire (BTU/hr)
| 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800
All Boilers Ouput At 60% Fire (BTU/hr)
| 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200
All Boilers Ouput At 80% Fire (BTU/hr)
| 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600
All Boilers Ouput At 100% Fire (BTU/hr)
| 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800
Hourly system efficiency
| 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | [9 empty] | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Boiler Gas Consumption (BTU/hr)
| 2473172.9435 | 2638051.1397 | 2802929.336 | 2802929.336 | 2967807.5322 | 2802929.336 | 2638051.1397 | 2473172.9435 | 1978538.3548 | 1483903.7661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1154147.3736 | 1648781.9623 | 1813660.1586 | 2143416.551 | 2308294.7473
Month: |  |  | OCT |  |  |  | Number of Boilers Choosen: |  |  | 4 |  | Average Monthly Efficiency: |  |  | 99.11% |  | Total BTU For Month: |  |  | 2493163072.5361
Day Hours
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Hourly Temperature °F
| 44 | 44 | 43 | 42 | 42 | 42 | 43 | 45 | 47 | 50 | 53 | 56 | 58 | 59 | 60 | 59 | 58 | 56 | 54 | 52 | 50 | 48 | 46 | 45
Outlet Water Temperature °F
| 106 | 106 | 107 | 109 | 109 | 109 | 107 | 105 | 102 | 97 | 93 | 89 | 86 | 84 | 83 | 84 | 86 | 89 | 91 | 94 | 97 | 100 | 103 | 105
Return Water Temperature °F
| 86 | 86 | 87 | 89 | 89 | 89 | 87 | 85 | 82 | 77 | 73 | 69 | 66 | 64 | 63 | 64 | 66 | 69 | 71 | 74 | 77 | 80 | 83 | 85
Efficiency at Current Inlet Water Temperature (20% Fire)
| 0.9911 | 0.9911 | 0.98995 | 0.98765 | 0.98765 | 0.98765 | 0.98995 | 0.99225 | 0.9957 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.998 | 0.99455 | 0.99225
Efficiency at Current Inlet Water Temperature (40% Fire)
| 0.9848 | 0.9848 | 0.9836 | 0.9812 | 0.9812 | 0.9812 | 0.9836 | 0.986 | 0.9896 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.992 | 0.9884 | 0.986
Efficiency at Current Inlet Water Temperature (60% Fire)
| 0.9765 | 0.9765 | 0.97525 | 0.97275 | 0.97275 | 0.97275 | 0.97525 | 0.97775 | 0.9815 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.984 | 0.98025 | 0.97775
Efficiency at Current Inlet Water Temperature (80% Fire)
| 0.9684 | 0.9684 | 0.9668 | 0.9636 | 0.9636 | 0.9636 | 0.9668 | 0.97 | 0.9748 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.978 | 0.9732 | 0.97
Efficiency at Current Inlet Water Temperature (100% Fire)
| 0.9582 | 0.9582 | 0.9564 | 0.9528 | 0.9528 | 0.9528 | 0.9564 | 0.96 | 0.9654 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.969 | 0.9636 | 0.96
Building Load (BTU/hr)
| 4273972.6027 | 4273972.6027 | 4438356.1644 | 4602739.726 | 4602739.726 | 4602739.726 | 4438356.1644 | 4109589.0411 | 3780821.9178 | 3287671.2329 | 2794520.5479 | 2301369.863 | 1972602.7397 | 1808219.1781 | 1643835.6164 | 1808219.1781 | 1972602.7397 | 2301369.863 | 2630136.9863 | 2958904.1096 | 3287671.2329 | 3616438.3562 | 3945205.4795 | 4109589.0411
All Boilers Ouput At 20% Fire (BTU/hr)
| 3171520 | 3171520 | 3167840 | 3160480 | 3160480 | 3160480 | 3167840 | 3175200 | 3186240 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3190400 | 3193600 | 3182560 | 3175200
All Boilers Ouput At 40% Fire (BTU/hr)
| 6302720 | 6302720 | 6295040 | 6279680 | 6279680 | 6279680 | 6295040 | 6310400 | 6333440 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6380800 | 6348800 | 6325760 | 6310400
All Boilers Ouput At 60% Fire (BTU/hr)
| 9374400 | 9374400 | 9362400 | 9338400 | 9338400 | 9338400 | 9362400 | 9386400 | 9422400 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9571200 | 9446400 | 9410400 | 9386400
All Boilers Ouput At 80% Fire (BTU/hr)
| 12395520 | 12395520 | 12375040 | 12334080 | 12334080 | 12334080 | 12375040 | 12416000 | 12477440 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12761600 | 12518400 | 12456960 | 12416000
All Boilers Ouput At 100% Fire (BTU/hr)
| 13798080 | 13798080 | 13772160 | 13720320 | 13720320 | 13720320 | 13772160 | 13824000 | 13901760 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 14356800 | 13953600 | 13875840 | 13824000
Hourly system efficiency
| 0.9848 | 0.9848 | 0.9836 | 0.9812 | 0.9812 | 0.9812 | 0.9836 | 0.986 | 0.9896 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.992 | 0.9884 | 0.986
Boiler Gas Consumption (BTU/hr)
| 4339939.686 | 4339939.686 | 4512358.8495 | 4690929.1949 | 4690929.1949 | 4690929.1949 | 4512358.8495 | 4167940.204 | 3820555.6971 | 3297563.9247 | 2802929.336 | 2308294.7473 | 1978538.3548 | 1813660.1586 | 1648781.9623 | 1813660.1586 | 1978538.3548 | 2308294.7473 | 2638051.1397 | 2967807.5322 | 3297563.9247 | 3645603.1816 | 3991506.9602 | 4167940.204
Month: |  |  | NOV |  |  |  | Number of Boilers Choosen: |  |  | 4 |  | Average Monthly Efficiency: |  |  | 97.66% |  | Total BTU For Month: |  |  | 3632476906.0522
Day Hours
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Hourly Temperature °F
| 36 | 35 | 34 | 34 | 34 | 34 | 35 | 36 | 38 | 40 | 43 | 45 | 47 | 48 | 48 | 48 | 47 | 45 | 43 | 41 | 40 | 38 | 37 | 36
Outlet Water Temperature °F
| 118 | 119 | 121 | 121 | 121 | 121 | 119 | 118 | 115 | 112 | 107 | 105 | 102 | 100 | 100 | 100 | 102 | 105 | 107 | 110 | 112 | 115 | 116 | 118
Return Water Temperature °F
| 98 | 99 | 101 | 101 | 101 | 101 | 99 | 98 | 95 | 92 | 87 | 85 | 82 | 80 | 80 | 80 | 82 | 85 | 87 | 90 | 92 | 95 | 96 | 98
Efficiency at Current Inlet Water Temperature (20% Fire)
| 0.9773 | 0.97615 | 0.96578 | 0.96578 | 0.96578 | 0.96578 | 0.97615 | 0.9773 | 0.98075 | 0.9842 | 0.98995 | 0.99225 | 0.9957 | 0.998 | 0.998 | 0.998 | 0.9957 | 0.99225 | 0.98995 | 0.9865 | 0.9842 | 0.98075 | 0.9796 | 0.9773
Efficiency at Current Inlet Water Temperature (40% Fire)
| 0.9704 | 0.9692 | 0.95983 | 0.95983 | 0.95983 | 0.95983 | 0.9692 | 0.9704 | 0.974 | 0.9776 | 0.9836 | 0.986 | 0.9896 | 0.992 | 0.992 | 0.992 | 0.9896 | 0.986 | 0.9836 | 0.98 | 0.9776 | 0.974 | 0.9728 | 0.9704
Efficiency at Current Inlet Water Temperature (60% Fire)
| 0.9615 | 0.96025 | 0.95188 | 0.95188 | 0.95188 | 0.95188 | 0.96025 | 0.9615 | 0.96525 | 0.969 | 0.97525 | 0.97775 | 0.9815 | 0.984 | 0.984 | 0.984 | 0.9815 | 0.97775 | 0.97525 | 0.9715 | 0.969 | 0.96525 | 0.964 | 0.9615
Efficiency at Current Inlet Water Temperature (80% Fire)
| 0.9492 | 0.9476 | 0.94257 | 0.94257 | 0.94257 | 0.94257 | 0.9476 | 0.9492 | 0.954 | 0.9588 | 0.9668 | 0.97 | 0.9748 | 0.978 | 0.978 | 0.978 | 0.9748 | 0.97 | 0.9668 | 0.962 | 0.9588 | 0.954 | 0.9524 | 0.9492
Efficiency at Current Inlet Water Temperature (100% Fire)
| 0.9366 | 0.9348 | 0.9323 | 0.9323 | 0.9323 | 0.9323 | 0.9348 | 0.9366 | 0.942 | 0.9474 | 0.9564 | 0.96 | 0.9654 | 0.969 | 0.969 | 0.969 | 0.9654 | 0.96 | 0.9564 | 0.951 | 0.9474 | 0.942 | 0.9402 | 0.9366
Building Load (BTU/hr)
| 5589041.0959 | 5753424.6575 | 5917808.2192 | 5917808.2192 | 5917808.2192 | 5917808.2192 | 5753424.6575 | 5589041.0959 | 5260273.9726 | 4931506.8493 | 4438356.1644 | 4109589.0411 | 3780821.9178 | 3616438.3562 | 3616438.3562 | 3616438.3562 | 3780821.9178 | 4109589.0411 | 4438356.1644 | 4767123.2877 | 4931506.8493 | 5260273.9726 | 5424657.5342 | 5589041.0959
All Boilers Ouput At 20% Fire (BTU/hr)
| 3127360 | 3123680 | 3090506.6667 | 3090506.6667 | 3090506.6667 | 3090506.6667 | 3123680 | 3127360 | 3138400 | 3149440 | 3167840 | 3175200 | 3186240 | 3193600 | 3193600 | 3193600 | 3186240 | 3175200 | 3167840 | 3156800 | 3149440 | 3138400 | 3134720 | 3127360
All Boilers Ouput At 40% Fire (BTU/hr)
| 6210560 | 6202880 | 6142933.3333 | 6142933.3333 | 6142933.3333 | 6142933.3333 | 6202880 | 6210560 | 6233600 | 6256640 | 6295040 | 6310400 | 6333440 | 6348800 | 6348800 | 6348800 | 6333440 | 6310400 | 6295040 | 6272000 | 6256640 | 6233600 | 6225920 | 6210560
All Boilers Ouput At 60% Fire (BTU/hr)
| 9230400 | 9218400 | 9138080 | 9138080 | 9138080 | 9138080 | 9218400 | 9230400 | 9266400 | 9302400 | 9362400 | 9386400 | 9422400 | 9446400 | 9446400 | 9446400 | 9422400 | 9386400 | 9362400 | 9326400 | 9302400 | 9266400 | 9254400 | 9230400
All Boilers Ouput At 80% Fire (BTU/hr)
| 12149760 | 12129280 | 12064853.3333 | 12064853.3333 | 12064853.3333 | 12064853.3333 | 12129280 | 12149760 | 12211200 | 12272640 | 12375040 | 12416000 | 12477440 | 12518400 | 12518400 | 12518400 | 12477440 | 12416000 | 12375040 | 12313600 | 12272640 | 12211200 | 12190720 | 12149760
All Boilers Ouput At 100% Fire (BTU/hr)
| 13487040 | 13461120 | 13425120 | 13425120 | 13425120 | 13425120 | 13461120 | 13487040 | 13564800 | 13642560 | 13772160 | 13824000 | 13901760 | 13953600 | 13953600 | 13953600 | 13901760 | 13824000 | 13772160 | 13694400 | 13642560 | 13564800 | 13538880 | 13487040
Hourly system efficiency
| 0.9704 | 0.9692 | 0.95983 | 0.95983 | 0.95983 | 0.95983 | 0.9692 | 0.9704 | 0.974 | 0.9776 | 0.9836 | 0.986 | 0.9896 | 0.992 | 0.992 | 0.992 | 0.9896 | 0.986 | 0.9836 | 0.98 | 0.9776 | 0.974 | 0.9728 | 0.9704
Boiler Gas Consumption (BTU/hr)
| 5759522.976 | 5936261.5121 | 6165453.953 | 6165453.953 | 6165453.953 | 6165453.953 | 5936261.5121 | 5759522.976 | 5400691.9637 | 5044503.7329 | 4512358.8495 | 4167940.204 | 3820555.6971 | 3645603.1816 | 3645603.1816 | 3645603.1816 | 3820555.6971 | 4167940.204 | 4512358.8495 | 4864411.518 | 5044503.7329 | 5400691.9637 | 5576333.814 | 5759522.976
Month: |  |  | DEC |  |  |  | Number of Boilers Choosen: |  |  | 4 |  | Average Monthly Efficiency: |  |  | 94.32% |  | Total BTU For Month: |  |  | 5317964851.4599
Day Hours
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Hourly Temperature °F
| 25 | 24 | 24 | 23 | 23 | 24 | 24 | 25 | 27 | 29 | 31 | 34 | 35 | 36 | 37 | 36 | 35 | 34 | 32 | 30 | 29 | 28 | 27 | 26
Outlet Water Temperature °F
| 134 | 135 | 135 | 137 | 137 | 135 | 135 | 134 | 131 | 128 | 125 | 121 | 119 | 118 | 116 | 118 | 119 | 121 | 123 | 126 | 128 | 129 | 131 | 132
Return Water Temperature °F
| 114 | 115 | 115 | 117 | 117 | 115 | 115 | 114 | 111 | 108 | 105 | 101 | 99 | 98 | 96 | 98 | 99 | 101 | 103 | 106 | 108 | 109 | 111 | 112
Efficiency at Current Inlet Water Temperature (20% Fire)
| 0.9413 | 0.93942 | 0.93942 | 0.93565 | 0.93565 | 0.93942 | 0.93942 | 0.9413 | 0.94695 | 0.9526 | 0.95825 | 0.96578 | 0.97615 | 0.9773 | 0.9796 | 0.9773 | 0.97615 | 0.96578 | 0.96202 | 0.95637 | 0.9526 | 0.95072 | 0.94695 | 0.94507
Efficiency at Current Inlet Water Temperature (40% Fire)
| 0.936 | 0.93417 | 0.93417 | 0.9305 | 0.9305 | 0.93417 | 0.93417 | 0.936 | 0.9415 | 0.947 | 0.9525 | 0.95983 | 0.9692 | 0.9704 | 0.9728 | 0.9704 | 0.9692 | 0.95983 | 0.95617 | 0.95067 | 0.947 | 0.94517 | 0.9415 | 0.93967
Efficiency at Current Inlet Water Temperature (60% Fire)
| 0.9287 | 0.92692 | 0.92692 | 0.92335 | 0.92335 | 0.92692 | 0.92692 | 0.9287 | 0.93405 | 0.9394 | 0.94475 | 0.95188 | 0.96025 | 0.9615 | 0.964 | 0.9615 | 0.96025 | 0.95188 | 0.94832 | 0.94297 | 0.9394 | 0.93762 | 0.93405 | 0.93227
Efficiency at Current Inlet Water Temperature (80% Fire)
| 0.9196 | 0.91783 | 0.91783 | 0.9143 | 0.9143 | 0.91783 | 0.91783 | 0.9196 | 0.9249 | 0.9302 | 0.9355 | 0.94257 | 0.9476 | 0.9492 | 0.9524 | 0.9492 | 0.9476 | 0.94257 | 0.93903 | 0.93373 | 0.9302 | 0.92843 | 0.9249 | 0.92313
Efficiency at Current Inlet Water Temperature (100% Fire)
| 0.9102 | 0.9085 | 0.9085 | 0.9051 | 0.9051 | 0.9085 | 0.9085 | 0.9102 | 0.9153 | 0.9204 | 0.9255 | 0.9323 | 0.9348 | 0.9366 | 0.9402 | 0.9366 | 0.9348 | 0.9323 | 0.9289 | 0.9238 | 0.9204 | 0.9187 | 0.9153 | 0.9136
Building Load (BTU/hr)
| 7397260.274 | 7561643.8356 | 7561643.8356 | 7726027.3973 | 7726027.3973 | 7561643.8356 | 7561643.8356 | 7397260.274 | 7068493.1507 | 6739726.0274 | 6410958.9041 | 5917808.2192 | 5753424.6575 | 5589041.0959 | 5424657.5342 | 5589041.0959 | 5753424.6575 | 5917808.2192 | 6246575.3425 | 6575342.4658 | 6739726.0274 | 6904109.589 | 7068493.1507 | 7232876.7123
All Boilers Ouput At 20% Fire (BTU/hr)
| 3012160 | 3006133.3333 | 3006133.3333 | 2994080 | 2994080 | 3006133.3333 | 3006133.3333 | 3012160 | 3030240 | 3048320 | 3066400 | 3090506.6667 | 3123680 | 3127360 | 3134720 | 3127360 | 3123680 | 3090506.6667 | 3078453.3333 | 3060373.3333 | 3048320 | 3042293.3333 | 3030240 | 3024213.3333
All Boilers Ouput At 40% Fire (BTU/hr)
| 5990400 | 5978666.6667 | 5978666.6667 | 5955200 | 5955200 | 5978666.6667 | 5978666.6667 | 5990400 | 6025600 | 6060800 | 6096000 | 6142933.3333 | 6202880 | 6210560 | 6225920 | 6210560 | 6202880 | 6142933.3333 | 6119466.6667 | 6084266.6667 | 6060800 | 6049066.6667 | 6025600 | 6013866.6667
All Boilers Ouput At 60% Fire (BTU/hr)
| 8915520 | 8898400 | 8898400 | 8864160 | 8864160 | 8898400 | 8898400 | 8915520 | 8966880 | 9018240 | 9069600 | 9138080 | 9218400 | 9230400 | 9254400 | 9230400 | 9218400 | 9138080 | 9103840 | 9052480 | 9018240 | 9001120 | 8966880 | 8949760
All Boilers Ouput At 80% Fire (BTU/hr)
| 11770880 | 11748266.6667 | 11748266.6667 | 11703040 | 11703040 | 11748266.6667 | 11748266.6667 | 11770880 | 11838720 | 11906560 | 11974400 | 12064853.3333 | 12129280 | 12149760 | 12190720 | 12149760 | 12129280 | 12064853.3333 | 12019626.6667 | 11951786.6667 | 11906560 | 11883946.6667 | 11838720 | 11816106.6667
All Boilers Ouput At 100% Fire (BTU/hr)
| 13106880 | 13082400 | 13082400 | 13033440 | 13033440 | 13082400 | 13082400 | 13106880 | 13180320 | 13253760 | 13327200 | 13425120 | 13461120 | 13487040 | 13538880 | 13487040 | 13461120 | 13425120 | 13376160 | 13302720 | 13253760 | 13229280 | 13180320 | 13155840
Hourly system efficiency
| 0.9287 | 0.92692 | 0.92692 | 0.92335 | 0.92335 | 0.92692 | 0.92692 | 0.9287 | 0.93405 | 0.9394 | 0.94475 | 0.95983 | 0.9692 | 0.9704 | 0.9728 | 0.9704 | 0.9692 | 0.95983 | 0.94832 | 0.94297 | 0.9394 | 0.93762 | 0.93405 | 0.93227
Boiler Gas Consumption (BTU/hr)
| 7965177.4243 | 8157846.4468 | 8157846.4468 | 8367387.6615 | 8367387.6615 | 8157846.4468 | 8157846.4468 | 7965177.4243 | 7567574.7023 | 7174500.7743 | 6785878.7024 | 6165453.953 | 5936261.5121 | 5759522.976 | 5576333.814 | 5759522.976 | 5936261.5121 | 6165453.953 | 6587014.1927 | 6973038.0704 | 7174500.7743 | 7363467.2191 | 7567574.7023 | 7758377.4803

## VTG EFF (hidden)
Return Water Temp
[15 empty] | 80°F |  |  |  |  | 100°F |  |  |  |  | 120°F |  |  |  |  | 140°F |  |  |  |  | 160°F
Interpolated Efficiency Data |  | Firing Rate | [5 empty] | Selected Boiler Efficiency Table |  |  |  |  | Model | Max Input | 20% | 40% | 60% | 80% | 100% | 20% | 40% | 60% | 80% | 100% | 20% | 40% | 60% | 80% | 100% | 20% | 40% | 60% | 80% | 100% | 20% | 40% | 60% | 80% | 100%
|  | 20% | 40% | 60% | 80% | 100% |  | Return Water Temperature |  |  |  |  | VTG-2000 | 2000000 | 99.7 | 99.1 | 98.4 | 97.1 | 95.8 | 97.5 | 96.8 | 95.9 | 94.6 | 93.4 | 93 | 92.5 | 91.8 | 91 | 90 | 89.2 | 88.8 | 88.5 | 88 | 87.6 | 88 | 87.7 | 87.3 | 86.8 | 86.3
| 78 | 99.7 | 99.1 | 98.4 | 97.1 | 95.8 |  | 80 | 100 | 120 | 140 | 160 |  | 2500000
| 79 | 99.7 | 99.1 | 98.4 | 97.1 | 95.8 | 20% | 99.8 | 97.5 | 93 | 89.2 | 88 | VTG-3000 | 3000000 | 99.8 | 99.2 | 98.4 | 97.3 | 96.2 | 97.5 | 96.8 | 95.9 | 94.7 | 93.3 | 93 | 92.5 | 91.8 | 90.9 | 90 | 89.2 | 88.9 | 88.5 | 88 | 87.5 | 88 | 87.7 | 87.3 | 86.8 | 86.3
| 80 | 99.8 | 99.2 | 98.4 | 97.8 | 96.9 | 40% | 99.2 | 96.8 | 92.5 | 88.9 | 87.7 |  | 3500000
| 81 | 99.685 | 99.08 | 98.275 | 97.64 | 96.72 | 60% | 98.4 | 95.9 | 91.8 | 88.5 | 87.3 | VTG-4000 | 4000000 | 99.8 | 99.2 | 98.4 | 97.8 | 96.9 | 97.5 | 96.8 | 95.9 | 94.6 | 93.3 | 93 | 92.5 | 91.8 | 90.9 | 90 | 89.2 | 88.9 | 88.5 | 88 | 87.5 | 88 | 87.7 | 87.3 | 86.8 | 86.3
| 82 | 99.57 | 98.96 | 98.15 | 97.48 | 96.54 | 80% | 97.8 | 94.6 | 90.9 | 88 | 86.8 | VTG-5000 | 5000000 | 99.2 | 98.5 | 97.7 | 96.9 | 96 | 96.8 | 95.9 | 94.6 | 93.3 | 92.5 | 92.5 | 92 | 90.9 | 90 | 89.4 | 88.9 | 88.6 | 88 | 87.5 | 87 | 87.7 | 87.4 | 86.7 | 86.3 | 86.1
| 83 | 99.455 | 98.84 | 98.025 | 97.32 | 96.36 | 100% | 96.9 | 93.3 | 90 | 87.5 | 86.3 | VTG-6000 | 6000000 | 99 | 98 | 97 | 96 | 95 | 96.5 | 95 | 93.4 | 92.8 | 92 | 93 | 92.5 | 91.8 | 91 | 90 | 88.8 | 88.3 | 88 | 87.8 | 87.5 | 88.4 | 88 | 87.6 | 87.4 | 86.9
| 84 | 99.34 | 98.72 | 97.9 | 97.16 | 96.18
| 85 | 99.225 | 98.6 | 97.775 | 97 | 96
| 86 | 99.11 | 98.48 | 97.65 | 96.84 | 95.82 |  | Selected Boiler Rated Natural Gas Input BTU/hr
| 87 | 98.995 | 98.36 | 97.525 | 96.68 | 95.64 |  | 4000000
| 88 | 98.88 | 98.24 | 97.4 | 96.52 | 95.46
| 89 | 98.765 | 98.12 | 97.275 | 96.36 | 95.28
| 90 | 98.65 | 98 | 97.15 | 96.2 | 95.1
| 91 | 98.535 | 97.88 | 97.025 | 96.04 | 94.92
| 92 | 98.42 | 97.76 | 96.9 | 95.88 | 94.74
| 93 | 98.305 | 97.64 | 96.775 | 95.72 | 94.56
| 94 | 98.19 | 97.52 | 96.65 | 95.56 | 94.38
| 95 | 98.075 | 97.4 | 96.525 | 95.4 | 94.2
| 96 | 97.96 | 97.28 | 96.4 | 95.24 | 94.02
| 97 | 97.845 | 97.16 | 96.275 | 95.08 | 93.84
| 98 | 97.73 | 97.04 | 96.15 | 94.92 | 93.66
| 99 | 97.615 | 96.92 | 96.025 | 94.76 | 93.48
| 100 | 97.5 | 96.8 | 95.9 | 94.6 | 93.3
| 101 | 96.5783 | 95.9833 | 95.1883 | 94.2567 | 93.23
| 102 | 96.39 | 95.8 | 95.01 | 94.08 | 93.06
| 103 | 96.2017 | 95.6167 | 94.8317 | 93.9033 | 92.89
| 104 | 96.0133 | 95.4333 | 94.6533 | 93.7267 | 92.72
| 105 | 95.825 | 95.25 | 94.475 | 93.55 | 92.55
| 106 | 95.6367 | 95.0667 | 94.2967 | 93.3733 | 92.38
| 107 | 95.4483 | 94.8833 | 94.1183 | 93.1967 | 92.21
| 108 | 95.26 | 94.7 | 93.94 | 93.02 | 92.04
| 109 | 95.0717 | 94.5167 | 93.7617 | 92.8433 | 91.87
| 110 | 94.8833 | 94.3333 | 93.5833 | 92.6667 | 91.7
| 111 | 94.695 | 94.15 | 93.405 | 92.49 | 91.53
| 112 | 94.5067 | 93.9667 | 93.2267 | 92.3133 | 91.36
| 113 | 94.3183 | 93.7833 | 93.0483 | 92.1367 | 91.19
| 114 | 94.13 | 93.6 | 92.87 | 91.96 | 91.02
| 115 | 93.9417 | 93.4167 | 92.6917 | 91.7833 | 90.85
| 116 | 93.7533 | 93.2333 | 92.5133 | 91.6067 | 90.68
| 117 | 93.565 | 93.05 | 92.335 | 91.43 | 90.51
| 118 | 93.3767 | 92.8667 | 92.1567 | 91.2533 | 90.34
| 119 | 93.1883 | 92.6833 | 91.9783 | 91.0767 | 90.17
| 120 | 93 | 92.5 | 91.8 | 90.9 | 90
| 121 | 92.7994 | 92.3411 | 91.7194 | 90.9556 | 90.16
| 122 | 92.61 | 92.16 | 91.55 | 90.8 | 90.02
| 123 | 92.4206 | 91.9789 | 91.3806 | 90.6444 | 89.88
| 124 | 92.2311 | 91.7978 | 91.2111 | 90.4889 | 89.74
| 125 | 92.0417 | 91.6167 | 91.0417 | 90.3333 | 89.6
| 126 | 91.8522 | 91.4356 | 90.8722 | 90.1778 | 89.46
| 127 | 91.6628 | 91.2544 | 90.7028 | 90.0222 | 89.32
| 128 | 91.4733 | 91.0733 | 90.5333 | 89.8667 | 89.18
| 129 | 91.2839 | 90.8922 | 90.3639 | 89.7111 | 89.04
| 130 | 91.0944 | 90.7111 | 90.1944 | 89.5556 | 88.9
| 131 | 90.905 | 90.53 | 90.025 | 89.4 | 88.76
| 132 | 90.7156 | 90.3489 | 89.8556 | 89.2444 | 88.62
| 133 | 90.5261 | 90.1678 | 89.6861 | 89.0889 | 88.48
| 134 | 90.3367 | 89.9867 | 89.5167 | 88.9333 | 88.34
| 135 | 90.1472 | 89.8056 | 89.3472 | 88.7778 | 88.2
| 136 | 89.9578 | 89.6244 | 89.1778 | 88.6222 | 88.06
| 137 | 89.7683 | 89.4433 | 89.0083 | 88.4667 | 87.92
| 138 | 89.5789 | 89.2622 | 88.8389 | 88.3111 | 87.78
| 139 | 89.3894 | 89.0811 | 88.6694 | 88.1556 | 87.64
| 140 | 89.2 | 88.9 | 88.5 | 88 | 87.5
| 141 | 89.9598 | 89.607 | 89.1331 | 88.5452 | 87.9467
| 142 | 89.8567 | 89.5067 | 89.0367 | 88.4533 | 87.86
| 143 | 89.7535 | 89.4063 | 88.9402 | 88.3615 | 87.7733
| 144 | 89.6504 | 89.3059 | 88.8437 | 88.2696 | 87.6867
| 145 | 89.5472 | 89.2056 | 88.7472 | 88.1778 | 87.6
| 146 | 89.4441 | 89.1052 | 88.6507 | 88.0859 | 87.5133
| 147 | 89.3409 | 89.0048 | 88.5543 | 87.9941 | 87.4267
| 148 | 89.2378 | 88.9044 | 88.4578 | 87.9022 | 87.34
| 149 | 89.1346 | 88.8041 | 88.3613 | 87.8104 | 87.2533
| 150 | 89.0315 | 88.7037 | 88.2648 | 87.7185 | 87.1667
| 151 | 88.9283 | 88.6033 | 88.1683 | 87.6267 | 87.08
| 152 | 88.8252 | 88.503 | 88.0719 | 87.5348 | 86.9933
| 153 | 88.722 | 88.4026 | 87.9754 | 87.443 | 86.9067
| 154 | 88.6189 | 88.3022 | 87.8789 | 87.3511 | 86.82
| 155 | 88.5157 | 88.2019 | 87.7824 | 87.2593 | 86.7333
| 156 | 88.4126 | 88.1015 | 87.6859 | 87.1674 | 86.6467
| 157 | 88.3094 | 88.0011 | 87.5894 | 87.0756 | 86.56
| 158 | 88.2063 | 87.9007 | 87.493 | 86.9837 | 86.4733
| 159 | 88.1031 | 87.8004 | 87.3965 | 86.8919 | 86.3867
| 160 | 88 | 87.7 | 87.3 | 86.8 | 86.3

## BLD LOAD (hidden)
OUTDOOR TEMPERATURE | BUILDING LOAD
°F | BTU/hr
-20 | 14794520.5479
-19 | 14630136.9863
-18 | 14465753.4247
-17 | 14301369.863
-16 | 14136986.3014
-15 | 13972602.7397
-14 | 13808219.1781
-13 | 13643835.6164
-12 | 13479452.0548
-11 | 13315068.4932
-10 | 13150684.9315
-9 | 12986301.3699
-8 | 12821917.8082
-7 | 12657534.2466
-6 | 12493150.6849
-5 | 12328767.1233
-4 | 12164383.5616
-3 | 12000000
-2 | 11835616.4384
-1 | 11671232.8767
0 | 11506849.3151
1 | 11342465.7534
2 | 11178082.1918
3 | 11013698.6301
4 | 10849315.0685
5 | 10684931.5068
6 | 10520547.9452
7 | 10356164.3836
8 | 10191780.8219
9 | 10027397.2603
10 | 9863013.6986
11 | 9698630.137
12 | 9534246.5753
13 | 9369863.0137
14 | 9205479.4521
15 | 9041095.8904
16 | 8876712.3288
17 | 8712328.7671
18 | 8547945.2055
19 | 8383561.6438
20 | 8219178.0822
21 | 8054794.5205
22 | 7890410.9589
23 | 7726027.3973
24 | 7561643.8356
25 | 7397260.274
26 | 7232876.7123
27 | 7068493.1507
28 | 6904109.589
29 | 6739726.0274
30 | 6575342.4658
31 | 6410958.9041
32 | 6246575.3425
33 | 6082191.7808
34 | 5917808.2192
35 | 5753424.6575
36 | 5589041.0959
37 | 5424657.5342
38 | 5260273.9726
39 | 5095890.411
40 | 4931506.8493
41 | 4767123.2877
42 | 4602739.726
43 | 4438356.1644
44 | 4273972.6027
45 | 4109589.0411
46 | 3945205.4795
47 | 3780821.9178
48 | 3616438.3562
49 | 3452054.7945
50 | 3287671.2329
51 | 3123287.6712
52 | 2958904.1096
53 | 2794520.5479
54 | 2630136.9863
55 | 2465753.4247
56 | 2301369.863
57 | 2136986.3014
58 | 1972602.7397
59 | 1808219.1781
60 | 1643835.6164
61 | 1479452.0548
62 | 1315068.4932
63 | 1150684.9315
64 | 986301.3699
65 | 821917.8082
66 | 657534.2466
67 | 493150.6849
68 | 328767.1233
69 | 164383.5616
70 | 0
71 | 0
72 | 0
73 | 0
74 | 0
75 | 0
76 | 0
77 | 0
78 | 0
79 | 0
80 | 0

## OUTDOOR RESET (hidden)
AMBIENT T1 | 0 |  | m | -1.4545
OUTLET WATER SET 1 | 170 |  | q | 170
AMBIENT T2 | 55
OUTLET WATER SET 2 | 90
OUTDOOR T | OUTLET WATER T | INLET WATER TEMPERATURE
°F | °F | °F
80 | 54 | 36
79 | 55 | 37
78 | 57 | 39
77 | 58 | 40
76 | 59 | 41
75 | 61 | 43
74 | 62 | 44
73 | 64 | 46
72 | 65 | 47
71 | 67 | 49
70 | 68 | 50
69 | 70 | 52
68 | 71 | 53
67 | 73 | 55
66 | 74 | 56
65 | 75 | 57
64 | 77 | 59
63 | 78 | 60
62 | 80 | 62
61 | 81 | 63
60 | 83 | 65
59 | 84 | 66
58 | 86 | 68
57 | 87 | 69
56 | 89 | 71
55 | 90 | 72
54 | 91 | 73
53 | 93 | 75
52 | 94 | 76
51 | 96 | 78
50 | 97 | 79
49 | 99 | 81
48 | 100 | 82
47 | 102 | 84
46 | 103 | 85
45 | 105 | 87
44 | 106 | 88
43 | 107 | 89
42 | 109 | 91
41 | 110 | 92
40 | 112 | 94
39 | 113 | 95
38 | 115 | 97
37 | 116 | 98
36 | 118 | 100
35 | 119 | 101
34 | 121 | 103
33 | 122 | 104
32 | 123 | 105
31 | 125 | 107
30 | 126 | 108
29 | 128 | 110
28 | 129 | 111
27 | 131 | 113
26 | 132 | 114
25 | 134 | 116
24 | 135 | 117
23 | 137 | 119
22 | 138 | 120
21 | 139 | 121
20 | 141 | 123
19 | 142 | 124
18 | 144 | 126
17 | 145 | 127
16 | 147 | 129
15 | 148 | 130
14 | 150 | 132
13 | 151 | 133
12 | 153 | 135
11 | 154 | 136
10 | 155 | 137
9 | 157 | 139
8 | 158 | 140
7 | 160 | 142
6 | 161 | 143
5 | 163 | 145
4 | 164 | 146
3 | 166 | 148
2 | 167 | 149
1 | 169 | 151
0 | 170 | 152
-1 | 171 | 153
-2 | 173 | 155
-3 | 174 | 156
-4 | 176 | 158
-5 | 177 | 159
-6 | 179 | 161
-7 | 180 | 162
-8 | 182 | 164
-9 | 183 | 165
-10 | 185 | 167
-11 | 186 | 168
-12 | 187 | 169
-13 | 189 | 171
-14 | 190 | 172
-15 | 192 | 174
-16 | 193 | 175
-17 | 195 | 177
-18 | 196 | 178
-19 | 198 | 180
-20 | 199 | 181
-21 | 201 | 183
-22 | 202 | 184

## ROI (hidden)
Year | Rate | Cost New | Cost Old
1 | 2 | 687865.4455 | 800287.3371
2 | 2.06 | 708501.4089 | 824295.9572
3 | 2.1218 | 729756.4511 | 849024.836
4 | 2.1855 | 751649.1447 | 874495.581
5 | 2.251 | 774198.619 | 900730.4485
6 | 2.3185 | 797424.5776 | 927752.3619
7 | 2.3881 | 821347.3149 | 955584.9328
8 | 2.4597 | 845987.7344 | 984252.4808
9 | 2.5335 | 871367.3664 | 1013780.0552
10 | 2.6095 | 897508.3874 | 1044193.4568
11 | 2.6878 | 924433.639 | 1075519.2605
12 | 2.7685 | 952166.6482 | 1107784.8384
13 | 2.8515 | 980731.6476 | 1141018.3835
14 | 2.9371 | 1010153.5971 | 1175248.935
15 | 3.0252 | 1040458.205 | 1210506.4031
16 | 3.1159 | 1071671.9511 | 1246821.5952
17 | 3.2094 | 1103822.1097 | 1284226.243
18 | 3.3057 | 1136936.7729 | 1322753.0303
19 | 3.4049 | 1171044.8761 | 1362435.6212
20 | 3.507 | 1206176.2224 | 1403308.6898